# Laxou, updated on march 1st ,2003

# Warning

This document (see  summary) was achieved from an experience on the power transmission network  of the "Electricité de France", but the principles shown have a general scope and the particularities of the French network are only mentioned as examples.

It does not claim to supply direct, concrete solutions to all problems of network protections, but only the way to approach these problems.

Concrete solutions may be obtained from the documentation of each utility:

- standards of the international electrotechnical committee (IEC)

- British standards (BS)

- Deutsche Institute für Normung (DIN)

- American national standards Information (ANSI)

- NF standards from the "Association Française des normes" (AFNOR)

- Internal EDF standards, published by the Direction des Etudes et Recherches

- Manufacturers guidebooks for the various equipment

- Guidelines internal to each utility, including, e.g. at the EDF:

. doctrine notes describing protection plans [49]

. general operation rules [7], [9]

. construction guidelines for overhead lines[106], substations  [107], underground cables[108]

. standardised wiring diagrams [104]

. setting guides for protective relays and automatic control devices  [57] ,[61]

. programs for short circuit current reckoning  [50], [99], [109]

. folder of asset characteristic [110]

This document could be used to analyse standards and instructions, and to elaborate internal guidelines. It could also be used by non - specialists who would like to have a qualitative idea of the problems treated.

Among the equipment noticed, you can find as well old-fashioned equipment as new or experimental equipment, to show the evolution of principles and technologies.

|  | Michel LAMI graduated from Grenoble University E.mail michel.lami@free.fr michel.lami@numericable.fr website: http://perso.numericable.fr/michlami http://michel.lami.free.fr |
| --- | --- |

Preface

Importance of the high voltage transmission network protective relays and automatic control devices for energy supply

In a power plant the aim of relays protecting electrical power equipment is to avoid any deterioration of this equipment in case of operation in bad condition, due to internal failures as insulation shortcomings, or regulation misworking. On well designed, well manufactured, well installed, well maintained, and well used power equipment they have to work very rarely. More, if a protective relay fails when a fault occurs, the damages caused to the protected generator or transformer may have important financial consequence for the utility, i. e. damaged power equipment repairing, and loss of production which must be replaced by generation from another plant, maybe more expensive, but generally have no consequence outside of the utility.

On the high voltage transmission network, the issue is quite different. Firstly an overhead line, which flies over the public property, undergoes periodically short circuits, due to lightning, unpruned trees, cranes, wind, pollution, ... .A good design of the line may minimise, but not suppress them. On the high voltage EDF network, we notice an average of 7 short circuits per year, and per 100 km.

Afterwards, a line which becomes more hot becomes longer, and its lowest point, between two towers, gets lower. It becomes dangerous for the neighbourhood. The consequences may then be calculated not only in financial losses, but in human lives. And that is the reason why all protective systems involve back-up dispositions, so as, in case of protective relay failure, the faulty high voltage equipment be led out of voltage in any case, whatever the consequences would be for the supply of a region.

A faulty behaviour of a protective relay may lead therefore to the outage of one or several customers, even of a whole town, including customers having priority (hospitals, fire brigade, ...). Now, when a manufacturer using a power supply of 10 MW is cut during e. g. 6 minutes, this does not mean only a non sold amount of energy of 1 MWh, but also a non - sold energy during maybe the several hours the manufacturer needs to work again; but it corresponds mainly to a displeased customer, who lost several hours of his production, and sometimes suffered some deterioration of his manufacturing equipment. If it concerns a big town, EDF must acknowledge, as a public service, to local and even national authorities.

At last, protective relays against network abnormal situations have a leading position to prevent network collapses, and the main effort of network controllers is done on these systems, as well as on the generator  regulators.

These different considerations show that the activity "protection and control" is at EDF as at any electrical energy  supplier, a strategic activity, of which depends the legitimacy of the utility towards the group of people, nation, region, town, it supplies.

(speech that I pronounced on October 30th, 1993, at the intention of two bosses having recently  in charge the protection and control of the high voltage network of the east of France, to explain them, vainly, why it was important.

Summary

Volume  1

Warning											page	1

Preface												3

Summary											5

Bibliography											13

Addresses											17

Index												19

First part:  GENERALITIES									21

1 - Transmission network (grid)								23

2 - Generalities on protective relays and automatic control devices                                  	29

3 - Measuring, metering and monitoring equipment						30

Second part:  MEASUREMENT REDUCERS						31

1 - Current transformers 									33

2 - Wound voltage transformers								47

3 - Capacitive voltage transformers 							49

4 - Safety problems concerning measurement reducers					51

5 - Commissioning									53

6 - Optical reducers									55

Third part:  PROTECTIVE RELAYS AGAINST SHORT CIRCUITS				57

1 - Protection fom short circuits of dead end networks					59

1 - 1 - 	Notion of selectivity								59

1 - 2 - 	Overcurrent protective relay							62

1 - 3 - 	Buchholz protective relay							63

1 - 4 - 	Earth - tank protective relay							64

1 - 5 - 	dead end line protective relay							65

1 - 6 - 	Earth - cable protective relay							67

1 - 7 - 	Condensator battery protective relay						68

1 - 8 - 	Protection against overvoltages and ferroresonance				70

1 - 9 - 	Overfluxing protective relay							73

1 - 10  	Functioning of the whole							74

2 - Protection from short circuits of meshed networks						77

2 - 1 - 	Distance protective relay							77

211 - 	Principle									77

2111 - 	Three - phase fault								77

21111 - 	Direction determination								77

21112 - 	Reactance comparison								78

21113 - 	Resistance comparison								79

21114 - 	Discrimination between short circuit and out - of - step				84

21115 - 	Recapitulation									85

21116 - Pick - up by overcurrent controlled by the voltage				86

2112 - 	Unbalanced short circuit							87

212 - 	Electromechanical protective relays						92

2121 - 	Pick - up									92

2122 - 	Phase selection									93

2123 - 	Distance measurement 								94

2124 - 	Directional relay								96

2125 - 	Out - of - step relay								96

2126 - 	Memory circuit - enclosing on a short - circuit					97

2127 - 	Zero sequence mutual induction compensation					97

2128 - 	Mho relay									98

2129 - 	Advantages and disadvantages of the electromechanical protective relays	99

213 -	Static protective relays								100

2131 - 	Phase comparators, one phase operation						100

2132 - 	Phase comparators, three phase operation					106

2133 - 	Mho characteristic, one phase operation						109

2134 - 	Mho characteristic, three phase operation					111

2135 - 	Advantages and disadvantages of the electronic protective relays		112

214 - 	Digital protective relays							113

215 - 	Carrier aided distance schemes							115

2151 - 	Principle of the different schemes						115

21511 - 	Transfer tripping								115

21512 - 	Permissive underreach transfer tripping						115

21513 -	Permissive overreach transfer tripping						116

21514 -	Acceleration scheme								116

21515 -	Zone extension									118

21516 - 	Blocking overreach								118

21517 - 	Unconditional remote tripping							119

21518 -	Echo and weak infeed mode							120

2152 - 	Application of these systems to three - ended lines				121

21521 - 	225 kV line, short symmetric dead end tee - point				121

21522 - 225 kV line, short symmetric live end tee - point					122

21523 -	225 kV line, long live or dead end tee - point					122

21524 -	63 kV or 90 kV	line								123

2153 -	400 kV	double lines								124

2154 - 	Compatibility between protective relays						125

2155 - 	Reliability of signalling channels						128

2156 - 	Telecommunication supports							130

22 - 	Phase comparison protective relay						133

23 - 	Differential protective relay							136

231 -	Overhead line differential protective relay					126

232 - 	Underground cable differential protective relay					138

233 -	Short connection differential protective relay					139

234 -	Busbar differential protective relay						140

2341 -	General principle 								140

2342 - 	High impedance and fixed threshold relay 					142

2343 - 	Middle impedance and percentage threshold relay				145

2344 - 	Low impedance relay supplied by performing reducers				147

2345 - 	Low impedance relay supplied by non specialised saturable reducers 		148

2346 - 	Middle impedance and low consumption relay					149

2347 - 	Busbar differential protective relay  with a linear combination of currents	149

2348 -	Particular precautions								150

2349 - 	Numerical busbar differential protective relay					151

24 - 	Zero sequence protective relay							152

Fourth part:

Protection from abnormal situations on the network , and automatic control devices	157

1 - 	Overload protection								159

2 - 	Protection from out - of - step operation						165

3 - 	Load shedding protection							167

4 -	Stuck breaker automatic device							169

5 -	Automatic recloser								171

6 -	Automatic loss of voltage device. ATRS					177

7 -	Automatic voltage regulation device						183

8 - 	Substation automatic device							189

# Fifth part: Functionning of the whole						191

1 - 	Protection plans against short circuits						193

11 - 	Constraints								193

111 -	Insulation co-ordination							193

112 -	Network stability							194

113 - 	Asset and gear behaviour						194

114 - 	Islanding time of the plants						195

115 - 	Presence of earth cables on the overhead lines				195

116 -	Quality of customer supply						196

12 - 	Elaboration principle							197

13 - 	Electromechanical plan							197

14 -	Static plan								198

2 -	Safeguard plan									203

3 -	Resilience plan									205

4 -	Network restoration plan							209

Sixth part:  SETTINGS	  								211

1 - Network calculation - principles							213

2 - Setting determination - preliminary							217

3 -Protection of two - ended overhead lines						219

31 -	Setting of distance protective relays					219

311 - 	Constraints due to the network						219

312 - 	Constraints due to switchgear and controlgear				222

313 - 	Constraints due to the relay						223

314 - 	Constraints due to the other relays					225

32 -	Setting of phase comparison relays					227

33 -	Setting of line differential relays					227

34 - 	Setting of zero sequence power relays					228

35 - 	Setting of dead end line relays						228

36 - 	Setting of earth - cable relays						229

37 - 	Setting of underground cable differential relays				230

38 - 	Setting of the stuck breaker automatic device				231

4 - Protection of three - ended overhead lines						233

41 - 	Power plant output  distance protective relay				233

42 - 	225 kV line, short symmetric dead end tee - point			233

43 - 	225 kV line, long dissymmetric dead end tee - point			234

44 - 	Schemes susceptible to provoke apparently evolutive short circuits	234

5 - Busbar protective relay								235

51 - 	Setting of a high impedance differential busbar relay			235

52 - 	Setting of a low impedance differential busbar relay			237

6 - Protection of coupling								239

61 - 	400 kV and 225 kV substations						239

62 - 	90 kV and 63 kV substations						239

7 - Protection of transformers								240

71 -	Protection of the high voltage side 					240

72 - 	Protection of the middle voltage side 					241

73 - 	Protection of the low voltage side					242

8 - Automatic control devices								243

Seventh part: Measuring, metering and monitoring EQUIPMENT.	245

1- Sensors										247

2 - Counters										251

21 - 	Countering installation by most important customers				251

22 - 	Countering installation by other customers					254

23 - 	International links and power plants with foreign participation			254

24 - 	Supply of utilities that do not belong to EDF					254

25 - 	Supply of distribution centres ((20 kV) belonging to EDF			254

3 - Event recorder									255	4 - Discordance recorder								257	5 - Fault Locator									259	6 - Quality recorder									261

Eighth part:  INSTALLATION   AND   OPERATION                         				263

1 - EDF standardisation, contractual documentation 					265

2- Cabling, precautions from overvoltages						266	3- Auxiliary power supply								268	4- Organisation of driving and monitoring						272	5- New bay commissioning								274	6- Preventive maintenance								277	7- Fault analysis. 									278	8- Troubleshooting.									282	9- Experience feedback.	 							283

Ninth part:  QUALITY OF ENERGY SUPPLY  				         			285

1 - Harmonics                                                                                                          	287

11 - 	Definition								287

12 - 	Origin of harmonics							287

13 - 	disadvantages due to harmonic distortions				290

14 - 	How may harmonic voltages be limited?				292

2 - Flicker										295

21 - 	Deviations inside the 0.5 to 25 Hz bandwidth				295

22 - 	Surges with several seconds interval					298

23 - 	Application: connection of an electric arc furnace to a network		300

3 - Unbalance										305

4 - Voltage holes and short interruptions							307

41 - Waveform of a customer's voltage supply					307

42 - Behaviour of a customer's installation					311

5 - Contractualisation of energy supply							319

Volume 2

Appendix 1 -  	Symmetric components

Appendix 2 - 	Determination of the apparent impedance and of the load reports during one phase and three phase automatic reclosure cycles.

Appendix  2-1 : Maximum transit current in case of three phase load report.

Appendix  2-2: Reckoning of the currents during a single phase reclosing cycle.

Appendix 3 - 	Overhead lines electrical characteristics

Appendix 4 - 	Current transformers choice criteria

Appendix 5 - 	Enclosure of a power transformer

Appendix 6 - 	Characteristics of some static distance protective relays

Appendix 7 -	Protection of thermal generators

Appendix 8 - 	Presentation of "UMBRELLA" program

Appendix 9 -	User's guide of the program "UMBRELLA"

Appendix 10 -	Setting of a teed line

# BIBLIOGRAPHY

[1]  Electrotechnical vocabulary, and particularly

# IEC 50-321 Measurement transformers - see also NFC  01-321

IEC 50-421 Power and wound transformers - see also NFC  01-421.

IEC 50 441 Apparatuses - see also  NFC  01-441

IEC 50 448 Protection of power networks - see also  NFC  01-448

IEC 50 601 Production, transmission, and distribution of electrical energy - see also  NFC  01-601

.

[2]  Symboles, and particularely

IEC  617-7 Apparatuses, and control equipment for protection - see also NFC  03-207.

[3]  Directives de construction des lignes, postes et canalisations souterraines - DEPT - EDF.

[4]  IEC 185 One -phase current transformers - see also NFC 42-502

[5]  IEC 186 One phase voltage transformers - see also NFC 42-501

[6]  Cahier des spécifications et conditions techniques des réducteurs de mesure - DEPT - EDF.

[7]  Règles générales d'exploitation - DEPT - EDF

[8]  UTE C 18 - 510 - AFNOR

[9]   Carnet de prescription au personnel - SPS - EDF

[10] Optical combined sensors, current and voltage - draft GEC-Alsthom.

[11] Non conventionnal current and voltage transformers, CIGRE CE/SE 34.

[12] Dispositif de protection par détection d'émission de gaz à deux contacts Buchholz - NFC 52-108.

[13] BS 142 - Electrical protective relay

[14] Relais de détection de gaz pour transformateur à bain d'huile - notice ABB.

[15] Les techniques de diagnostic et la maintenance - symposium CIGRE, BERLIN, Mai 93.

[16] Protection d'antenne passive - notice  ICE.

[17] Protection masse - câble PMCS 1 - notice ICE

[18] NFC 54 - 100 - Condensateurs de puissance

[19] Protection interne de transformateur PTP 3 000 - GEC-Alsthom

[20] Etude des différentes causes d'erreur de mesure susceptibles d'apparaître dans les protections

statiques type PDS 1 100 -Michel Lami - DEPT - EDF

[21] Généralité sur la protection des réseaux électriques - Marcel Pétard - Centre de formation des

Mureaux - EDF.

# [22] La protection du réseau français - Marcel Pétard - Revue Générale d'électricité (RGE) n° 21,

Septembre 1961.

[23] Protections et automatismes de réseau - René Sardin - CRTT Est - EDF.

[24] Protection de distance RXAP - notice Enertec.

[25] Protections de distance PD3A 6000 et PDS - notice Enertec.

[26] Protection de distance LZ 95 et RAZOA - notice ABB.

[27] Protections de distance PXLC et PXLP - notice GEC-Alsthom.

[28] Protection de distance numérique PXLN - notice Enertec.

[29] Protection de distance numérique  7SA 511 - notice Siemens.

[30] Protections de distance numériques REZ1, REL 100 et REL 316 - notice ABB.

[31] GEC measurement protective application guide.

[32] Téléactions haute et basse fréquence à grande sécurité - Système TGS - notices Techniphone.

[33] GEC P10 - user's book GEC  Alsthom.

[34] 7 SD 31 - user's book Siemens.

[35] DIFL - user's book GEC Alsthom.

[36] LFCB - user's book GEC Alsthom.

[37] DL 323 - user's book GEC Alsthom.

[38] PDLC 10 - user's book ICE.

[39] RADSS - user's book ABB.

[40] DIFB - user's book GEC Alsthom

[41] PMLS 345 - user's book ICE.

[42] PMCT 10 - user's book ICE.

[43] DRS 50 - 	user's book ICE.

[44] BEF 301 - 	user's book ICE.

[45] TADD- 	user's book ICE.

[46] PADD 3000 - user's book GEC Alsthom; TADD 1 - notice ICE.

[47] ATRS - user's book ICE

[48] TART - user's book ICE

[49] Les plans de protection du réseau de transport, Bernard Duchêne, DEPT, EDF

# [50] Stabilité des grands sites de production à l'horizon 87 sur défaut 225 kV, P. Vergerio,

M. De Pasquale, M. Lami, DEPT, EDF

[51] Evolution des protections du réseau de transport, journée d'étude SEE (voir RGE) du 3/10/85.

# [52] Circuits très haute tension et basse tension de liaison d'évacuation d'énergie des centrales

thermiques classiques et nucléaires, DEPT EDF, février 90, (dite brochure rouge)

# [53] conduite en régime dégradé, note explicative associée à la règle 90-04, Service des mouvements

d'énergie, (SME), EDF.

[54] Maquette du plan de défense coordonné, Direction des Etudes et recherches EDF, Ph. Denis, J.C.

# Bastide, M. Huchet, 20/3/92

[55] Cours de fonctionnement dynamique des réseaux, Direction des Etudes et Recherches EDF,

Service Etudes de réseau, Département Fonctionnement et Conduite des Réseaux.

# [56] Protection contre les défauts extérieurs des centrales hydrauliques, notes de doctrines XEL 02 10

et XEL 02 11, Direction Production Transport (DEPT), Jacques Lecouturier, 06/92.

[57] Guide de réglage des protections - DEPT EDF, 1993.(régulièrement remis à jour)

et notamment: Etude du comportement des protections de distance sur les lignes à trois extrémités D 633.91/BD/LB/n° 3002 de Bernard Duchêne.

[58] PSPT, user's book GEC Alsthom.

[59] RAKZB user's book ABB.

[60] PTP, user's book GEC Alsthom.

[61] Guide de réglage des automates, CRTT Est, EDF.

[62] Transducteurs de mesure électrique, user's book GEC Alsthom.

[63] Dossier d'identification et de maintenance, CDM3 et transducteurs de mesure, Chauvin-Arnoux.

[64] TEGETEC, user's book Schlumberger Industrie.

[65] FAN 1, user's book Landis et Gyr.

[66] PAS 692, user's book Techniphone.

[67] PAS-PCS 21, user's book CETT.

[68] ECP 80, user's book CETT.

[69] TPE 2000, user's book GEC Alsthom.

[70] SOREL EPC, user's book Arthus.

[71] DLD, user's book GEC Alsthom

[72] Qualimètre user's book Siemens.

[73] APR 8, user's book ANPICO

[74] Standard HN 46 R 01, called  "Dicot", standard EDF distibuted by the DER

# [75] Traitement des signalisations nécessaires à la conduite et à la surveillance des installations, called

Brochure violette, DEPT, EDF.

[76] Guides de mise en service, DEPT, EDF.

[77] Guides de maintenance, DEPT, EDF.

[78] Standard HN 33 S 34, DER.

[79] Directive H 115, DER.

[80] Perturbations électriques et électromagnétiques des circuits basse tension des postes et centrales,

Janvier 1980, distributed by the " division Instrumentation d'exploitation" of the DER.

[81] Guide de l'ingénierie électrique, by Gérard Solignac, éditions Lavoisier.

[82] Contrat pour la fourniture d'énergie au tarif vert, called contrat Emeraude, EDF, Service National.

# [83] Les moyens d'action et les téléinformations nécessaires pour la conduite du système production -

transport - consommation, called "brochure Saumon", DEPT, EDF.

# [84] Perturbations électriques, comportement des installations industrielles, Claude Mongars,

CRTT Est, EDF.

[85] Guide des erreurs à ne pas commettre, Michel Lami, CRTT Est, EDF (projet)

# [86] Exposé sur les réducteurs de mesure présenté lors des assises "plan de protection 225 kV"

organisées par la DEPT, D63/603 -  Benjamin Gaillet - 29/5/1980.

# [87] Les techniques de l'Ingénieur, D 135, mesures à très haute tension, Pascal Gayet and Jacques

Jouaire, 1979.

# [88] Les techniques de l'Ingénieur, D 4805, protection des réseaux de transport et de répartition,

Claude Corroyer and Pierre Duveau, 1995.

# [89] Les techniques de l'Ingénieur, D 69, réseaux électriques linéaires à constantes réparties,

Robert Bonnefille.

# [90] Les techniques de l'ingénieur, D 4421, contraintes de conception des lignes aériennes,

Yves Porcheron.

[91] Protective relays, their theory and practice, Van Warrigton, Chapman and Hall, 1962

# [92] Protective relay application guide, GEC, 1975

[93] Utilisation des protections contre les surtensions et la ferrorésonance dans les tranches des postes

# 400 kV en piquage existant sur une ligne double terne, EDF, DEPT, D 564/91-100 C du 9/8/94 -

Pierre Duveau

# [94] Exploitation d'un poste en antenne, calcul des surtensions en cas d'ouverture d'un poste à la

source, EDF, DER, HM/15-1152 JcK/CB du 12/3/87

[95] Système de protection contre la ferrorésonance, notice ICE.

[96] 7 TUD 15, notice Siemens

[97] Capacitive voltage transformers: transient overreach concerns and solutions for distance relaying

# Daqing Hou and Jeff Roberts, Schweitzer Engineering laboratories

[98] EPAC 3900, notice GEC Alsthom.

[99] Manuel d'utilisation d'EGERIE pour Windows; USI Ile de France.

[100] Protection PSEL 3003, notice GEC Alsthom

[101] Protection 7 SN 21, notice Siemens

[102] Mémoire Contrôle Electrique de l'USI Est, n°  22

[103] Comportement des protections complémentaires dans les réseaux de répartition HT, Michael

# Sommer, Université Paris XI, Orsay

[104] Schémathèque, Centre National d'ingénierie Réseau (CNIR), DEPT

# [105] Réglage des protections différentielles de câble, Benoît Lys, EDF, Production Transport, SIRA

[106] Directive de construction des lignes aériennes, Centre National d'ingénierie Réseau, DEPT

# [107] Directive de construction postes, Centre National d'ingénierie Réseau, DEPT

[108] Directive de construction des canalisations souterraines, CNIR, DEPT

[109] Programme Courcirc, DER, EDF

[110] Base Platine, DER, EDF

[111] Guide de mise en service, Centre National d'ingénierie Réseau (CNIR), DEPT

[112] draft D 6120 / 09 / n° 69 - SCE / HC / MCD "fonctionnement du réseau pendant un cycle de

réenclenchement monophasé, dec 72, CNIR (département essais) - DEPT

[113] draft 4002 / 54.FDQ 94 / JLL / n° 3045 " réglage des systèmes de protection des réseaux à 400

kV" , janvier 1996 - DEPT

[114] draft 6100 - 06 - 80 - 1572 LB - BGR / CM " programme CELINE" du 11 janvier 1988 - DER

[115] règles générales d"'exploitation - DEPT

[116] user's book Siemens 7 UM 511 generator protection relay (version V3)

[117] user's book Siemens 7 UM 512 generator protection relay (version V3)

[118] user's book Siemens 7 UM 516 generator protection relay (version V3)

[119] user's book Siemens protection numérique de surintensité et de surcharge SIPROTEC 7SJ600

[120] user's book Siemens 7 UT 512 / 513 differential protection relay (version V3) for transformers,

generators, motors ans short lines

[121] distance protective relay S 321 - 5, user's book Schweitzer

[122] the influence of substation busbar and circuit breaker arrangement upon the substation control

equipment design and reliability - CIGRE WG 23-05, Bengt Andersson, ABB relays AB,

S 72171  Västerås (sverige).

[123] Spécifications fonctionnelles et technologiques des protections et automates du réseau de

transport, DEPT, EDF.

[124] Code de travaux, Centre National d'ingénierie Réseau (CNIR), DEPT

[125] Marchés tarifs, Centre National d'ingénierie Réseau (CNIR), DEPT

[126]  Dossiers de tranche normalisée, Centre National d'ingénierie Réseau (CNIR), DEPT

[127]  Guide de mise en service de la tranche, Centre National d'ingénierie Réseau (CNIR), DEPT

[128]  Mesures électriques, Maurice Gaillet, 1959 (centre de perfectionnement électrique de Nanterre)

[129]  Référentiel technique du Réseau de Transport d’Energie. Site internet

http://www.rte-france.com/htm/fr/mediatheque/telecharge/reftech/15-07-06_complet.pdf

[130] arrêté technique du 17 mai 2001. Site internet

http://www.admi.net/jo/20010612/ECOI0100130A.html

[131] protection MICOM P 442 http://www.alstom.com/fr/grid/produits-et-services/solutions-pour-automatisation-de-poste/relais-de-protection/MiCOM-Alstom-P441-P442-P444/

# ADDRESSES

# Standards IEC - 1, Rue de Varembé, Genève, Suisse.

# Standards BS - 2, Park street, London W1A2BS.

Standards DIN - Deutsche Elektrotechnische Kommission im DIN und VDE, Burggrafenstrasse 4,Postfach 1107,	 D1000 Berlin 30

Standards ANSI - American National Standards Insitute, 1819L Street, NW, 6th FI. Washington DC 20036

Standards NF:  AFNOR - Gestion des ventes, tour Europe, Cedex 7, 92 049 Paris la Défense.

All standards may be afforded at this address.

CIGRE, 3 Rue de Metz, 75 010 Paris.

# RGE, 48, Rue de la Procession, 75 015 Paris.

# DEPT - EDF - Cedex 48, 92 068 Paris la Défense.

# EDF, Service National et Service des Mouvements d'énergie (SME), Rue Louis Murat, 75 384 Paris  Cedex 08.

# EDF, CRTT Est (ou USI Est), 8, Rue de Versigny, 54 521 Villers lès Nancy.

# EDF, Service Ingénierie Rhône Alpes(SIRA), 15, rue des Cuirassiers, BP 3074, 69399 Lyon Cedex 03

# EDF, USI Ile de France, 32, avenue Pierre Grenier, BP 401, 92 103 Boulogne Billancourt Cedex

# Direction des Etudes et Recherches (DER) - EDF - 1, Avenue du Général De Gaulle, 92 141 Clamart

# Service Prévention Sécurité (SPS) - EDF - CEDEX 08,  75 382 Paris.

# Les techniques de l'Ingénieur, 8, Place de l'Odéon, 75006 Paris

Manufacturers:

ALSTOM, alias GEC Alsthom, alias Enertec, alias Compagnie des Compteurs - 			Lotissement du fond de la Banquière, 34 970 Lattes.

GEC Measurement: voir même adresse, et aussi Saint Leonard's work, Stafford ST 174 LX, England

ICE (Industriel de contrôle et d'équipement), 11, rue Marcel Sembat, 94410 Alfortville France

# Techniphone - 31 Rue de l'Union, 78 600 Maisons Laffitte.

# ABB - S 72 171  Västerås, Sverige. ; CH 5401 Baden, Suisse; 6, Rue des Peupliers, 92 004 Nanterre

# Siemens - Humboldstrasse 59, EVSV PO BOX 4806, 8500 Nürnberg, Deutschland.

Anpico - 82 Rue du Quesnoy, 59 236 Frelinghien - représenté par Ecodime, zone des entrepôts  Juliette, 		94 310 Orly.

Chauvin- Arnoux, 190 Rue Championnet, 75 018 Paris.

# Schlumberger Industrie, BP 620 02, 50 Avenue Jean Jaurès, 92 542 Montrouge Cedex.

# Landis et Gyr Energy, 30, Avenue Pré Auriol, 03 100 Montluçon.(adresse en France)

# Techniphone, Boite Postale 22, 13 610 Le Puy Sainte Réparade.

# CETT ( Compagnie Européenne de télétransmision), 3, Parc des Grillons,

# Artus, 6, Rue du Docteur Schweitzer, 91 420 Morangis.

Schweitzer Engineering laboratories, 2350 NE Hopkins Court, Pullmann, WA 99163-5603, Washington, USA.

# INDEX

Acceleration scheme	3rd part, § 21514; 21531

Admittance diagram	3rd part, § 2128

Alternator		1st part, § 22  / Appendix 1, § 1; 23

Amplifier		2nd part, § 6 / 3rd part, § 213 / 8th part, § 5 / 9th part, § 231

Automatic device	1st part, § 23 / 3rd part, § 2347 / 4th part, § 4;§ 5; §6; §8 / 5th part, § 141, § 142 / 6th part, § 8

Autotransformer	1st part, § 1 / 3rd part, § 2332 / 5th part, § 14

Bay			1st part, § 1 / 8th part, § 5; § 6

Bistable relay		3rd part, § 2341

Blocking		3rd part, § 21516; § 21541

Carrier aided distance schemes		3rd part,§ 215 / 4th part, § 523; 8 / 5th part, § 141 / 6th part, § 2 / 8th part, § 32 / 9th part, § 53

Comparator		3th part, § 213; § 222

Compounding		4th part, § 72

Configurator		7th part, § 32

Creep			4th part, § 113

Delay	3rd part, § 12; § 2123; 2133; § 21541; § 21543 / 4th part, § 82 / 5th part, ,§ 4 / 6th part, § 38; 	§ 61; § 823

Derivator		3rd part, § 2135

Directional relay	3rd part, § 2124; 21313

Disturbance recorder	1st part, § 3 / 3rd part, § 214 / 8th part, § 32; § 7

displayed constant line	appendix 1 / appendix 3

Double phase - to - earth fault		3rd part, § 2153; § 2131

Earth cable		3rd part, §21321; 21562

Earth factor		3th part, § 2112 / 	Appendix 2

Electromotive force	2nd part, § 1 / 3rd part, § 212; 24 / 4th part, § 21

Event recorder		7th part, § 3; § 4 / 8th part, § 32; § 7

Ferroresonance		2nd part, § 2, 3rd partie, §18

Fuse breaking		3rd part, § 21123

Geometric line characteristics	Appendix 3

Impedance		2nd part, § 3 / 3rd part, § 11; § 2111; § 2112; § 2123; § 2133; § 21516 /

5th part, § 111 / 6th part, § 13 / 9th part, § 121; § 22; § 231; § 234

/ appendix 2

Inductance		2nd part, § 1; § 2;§ 3 / 3rd part, § 2121; § 2123; § 2127 / appendix 1, § 11

Integrator		3rd part, § 2135 / 7th part, § 12; § 15

Isolators		1st part, § 1 / 3rd part, § 234 / 8th part, § 2

Magnetic transducer	3rd part, § 2121

Matrix			6th part, § 1 / appendix 1 / appendix 3

Meter			1st part, § 32 / 2nd part, § 1 / 7th part, § 2 / 9th part, § 139

Mho relay		3rd part, § 2128; § 2133; § 2134

Microwave 		3rd part, § 21564; § 2132 / 5th part, § 312

Monostable 		3rd part, § 2131

Optical fibre 		3rd part, § 21563

Out - of - step		3rd part, § 21114 / 4th part, § 21

Out - of - step relay	3rd part, § 21113; § 2125; § 21326 / annexe 6

Overcurrent relay	3rd part, § 12, 8th part, § 75

Overfluxing	 	3rd part, § 19

Ovehead line	 	1st part, § 1; § 2 / 3rd part, § 16; § 21321; § 221; § 2321 /

4th part, § 11; § 511 /5th part, § 141

Peak voltage		4th part, § 22

Phase - to - phase - to eath fault		3th part, § 18; § 2112, appendix 6, §054

Pilot			3rd part, § 213; § 232 / appendix 6

Pilot cable		3rd part, § 2321

Power group		4th part, § 5212

Power line carrier 	3th part, § 21561

Power transformers	1st part, § 1; § 23 / 2nd part, § 1; § 2 / 3rd part, § 11; § 12; § 14; § 18; 2129 / 			6th part, § 3112 ; § 511 / 9th part, § 112; § 12; § 13; § 14; § 234 / appendix 5

Quality meter		1st part, § 33 / 7th part, § 6 / 9th part, § 54

Radiobeacon		3rd part, § 222

Reactance	3rd part, § 21111; § 2112; § 21311 / 5th part, § 111 / 6th part, § 31; § 42; § 71; §73 / 9th part, § 23

Reducer	2nd part / 3rd part, § 2135; § 222; § 2332; § 23423 / 6th part, § 73 / 7th part, § 14 / appendix 4

Regulator		4th part, § 31 / 8th part, § 32

Remote control		4th part, § 8 / 7th part, § 1 / 8th part, 32; § 4

Remote tripping	3th part, § 15; § 21517; § 21522; § 2155

Selectivity		3rd part, § 11

Self - inspection		3rd part, § 214

Sensor for remote measuring	7th part, § 1

Spark gap		3rd part, § 14, § 2347

Specialized link 	3rd part, § 21565

Switch			7th part, § 1

Synchrocoupling	4th part, § 524

Telecommunication	3rd part, § 215

Thyristor bridge	9th part, § 424

Topography		3rd part, § 2341

Underground cable	1st part, § 1 / 3rd part, § 232 / 4th part, § 13

Wiring			1st part, § 3 / 3rd part, § 2343 / 6th part, § 511 / 8th part, § 2

Zero sequence		3rd part, § 15; § 18; § 2112; § 2121; § 2127; § 21321; § 21521; § 21524; § 24 /

4th part, § 52122 / 5th part, § 142 / 6th part, § 13 / 8th part, § 7 / 9th part, § 131; § 134; 3 / appendix 1, § 23 / appendix 2

Zero sequence mutual inductance	3rd part, § 2127