FIRST PART

(by clicking above you return to the general summary)

# GENERALITIES

1 - TRANSMISSION NETWORKS

2 - GENERALITIES   ON THE  PROTECTIVE RELAYS AND AUTOMATIC CONTROL DEVICES

3 - MEASURING,  METERING  AND  MONITORING  EQUIPMENT

The electrical energy supplied to each of us  must be producted, transmitted, displayed and distributed.

The production is elaborated in France by important, mainly nuclear, power plants, to which must be added coal, oil and gaz thermal ones, and also hydraulic ones, situated on the big rivers and big dams. By the side of these types of production can be found also numerous souces of low unit power, scattered on the whole of the territory : little hydraulic power plants, windmills and photovolotaïc cells. These different modes of generation are not in competition, but complete each other to insure for the best the balance between production and consummation.

The transmission network is performed by 400 kV connections. These are generally overhead lines, exceptionnaly underground cables. The ends of these connections are situated in substations. High power plants supply a number of these substations. In most of them high power transformers  are found, which supply the 225 kV and 90 kV networks.

The whole of the 225 kV and 90 kV links form the display network. The links are mainly overhead lines, but they are progressively replaced by underground cables. They supply the substations which are situated near the places where the consumption is important.

In the display substations are located transformers, the lower voltage of which is 20 kV. The 20 kV links, generally underground cables, supply the manufactures and the district transformers, which supply the private persons in 220 V. These links and transformers form the distribution network.

All these assets work with a three phase voltage (3 phase cables) except the 220 V links which supply the private persons, and which work with a one phase voltage (one phase wire and one neutral wire). The reason of the use of the three phase voltage is given in the appendix 1.

The production and the transmission of the energy are managed by control centers, which insure on one hand the balance generation-consumption, by operating on the control of the big generators , and on another hand the display  of the energy fitted with the possibilities of the networks, by operating on the schemes of these networks. These functions are essential to supply correctly the different customers.

The target of this book is to describe the different systems of protection against any aggression undergone by the different assets of the transmission and display networks. It does not deal with the problems of the distribution networks. The protection of the big generators is also evocated.

These protection systems may be, following the cases, entirely autonomous, when the decision time is too short to allow a human intervention, or dependant of orders coming from the control center. These systems give a needfull help to the network controllers.

A scheme of the electric energy supply networks of France is given herunder.

1 - ENERGY supply networks

They are made of three-phase assets, namely: overhead lines, underground cables, power transformers and busbars, arranged according to the following diagram (the voltages and powers indicated are the ones currently used on the French network):

Generation                  	     hydraulic or    					Nuclear plant

Thermal plant			 		              alternator

power  250 MW 	    microplants			 power between

windmills			600 and 1400 MW

solar

Un  12 kV					              Un = 20 à 24 kV

Distribution

network

Un  225 kV					               Un = 400 kV

busbars 400 kV

Line 400 kV

Transmission									   Autotransformer 									                 400 / 225 kV

300 to 600 MVA

busbar 225 kv

Line 225 kV

busbar 225 kV

Line 225 kV						    Transformer

Display									    	    225 kV / 90 kV*

70 to 170 MVA

busbar 90 kV

Line 90 kV*						   Line 90 kV*

busbar 90 kV

Distribution

Transformer

Line 20 kV						   90 kV* / 20 kV

20 or 36 MVA

* or 63 kV, according to the regions

There are also power transformers allowing direct transformation from 400 kV  to  90 kV or 63 kV, or from 225 kV to  20 kV, as well as few 90 / 63 kV auto-transformers.

Concerning the currents, two reference levels are defined:

- permanent currents, to which are referred for determining heating of the assets;

- short circuit currents, which usually last only a few hundreds of milliseconds, and to which are referred for the resistance of assets to electrodynamic effects.

The rated values are:

400 KV       steady state current In = 2 kA or 3.15 kA     short circuit current Icc = 40 kA or 63 kA

225 KV       steady state current In = 1.25 kA or 2 kA    	short circuit current Icc = 31.5 kA

90 KV         steady state current In = 1 kA or 2 kA 	short circuit current

Icc = 20 kA or 31.5 kA  between phases

8 kA or 10 kA between  phase and earth

63 KV        idem

# Each asset is

- connected to - and disconnected from - the rest of the network by a circuit breaker, able to cut the short circuit current;

- linked to - or separated from - the rest of the network, power off, by visible cut - off gears: isolators.

- protected by protective relays and automatic control devices that detect short - circuits and abnormal situations in the network from currents circulating in the assets, and the voltages under which they are found. his equipment then activates the circuit breakers.

The relays and the automatic control devices do not use voltages and currents from the network, but values much lower that are proportional to them. Transformation is made by measurement reducers..

The different high voltage switchgears of the substation are grouped in cells, each of them including one circuit breaker. The whole of low voltage equipment of a cell is called a bay.

The EDF substations generally have the following high voltage diagram:

LINE CELL

Busbars of a substation							Busbar 1

Busbar 2

Isolators

X				Circuit breaker

Measurement reducers						     	protective relay and

automatic control device

earthing								Insulating isolator

isolator

Capacitive voltage transformer

Line trap

Overhead line

High voltage circuit  (one line = 3 phases)

Measurement circuit ( 	"	"	" )

Control circuit

transformer  CELLS

Busbar 1

busbars

of the higher voltage						Busbar 2

substation

Other

bays								Switching isolators

differential busbar protec-

tive relay of the substation			 X		Higher voltage circuit breaker (hvcb)

higher voltage current transformer

POWER  Transformer

earth - tank relay						lower voltage Current transformer

wound voltage tansformer

to hvcb      to lvcb

Protective relays and

automatic control devices

differential relay of the 							at the lower voltage subst.

link

Current transformer at the lower

voltage substation

X

to hvcb							lower voltage circuit breaker (lvcb)

Switching isolator

Busbars of the lower						Busbar 1

voltage substation

Busbar 2

Coupling BETWEEN BUSBARS

coupling isolator

busbar 2

X	coupling

circuit breaker					     capacitive voltage transformer

(on one phase only)

current transformer

busbar 1

protective

relays and

automatic

devices					capacitive voltage transformer

(on each of the three phases)

Note please:

the protective relays may be used either as a coupling protection or as a line protection. In the latter case a busbar is assigned to a single line whose circuit - breaker is short - circuited and the protective relay disabled. It may then be said that the coupling is used in transfer.

SeGMENTing

# Large substations may include four busbars

Busbar A1			T1		     Busbar B1

X

X									X

C1										C2

Busbar A2					      Busbar B2

X

T2

C1 and C2 are couplings treated as above.

T1 and T2 are segmenting. They cannot be used in transfer.

# Note please 1: notion of electrical node

It is a whole of busbars, able to be disconnected from the network by circuit breakers, but unable to be itself split by a circuit breaker. It generally includes one busbar, but sometimes more.

For example, on figure 5, the busbars A1 and A2 form two nodes, but they may form only one node, when both switching isolators of the same cell are closed, when a line is disconnected from the busbar A1 and connected to the busbar A2 (or the contrary): during a few seconds, both isolators are simultaneously closed.

On some substations, the busbars are displayed as above, but the circuit breakers at T1 ad T2 are replaced by isolators. Busbars A1 and B1 form only one electrical node, and so do busbars A2 and B2. The substation is formed of only 2 nodes.

It will be seen that this concept is important to perform the busbar differential protective relays

Note please 2:

There are also other substation diagrams abroad: ringbus substations, substations with one and half circuit breaker per bay, substations with transfer busbar. Each has its advantages and disavantages, but it is important not to mix types of substations in the same network. [122]

2 -GENERALITIES  ON PROTECTIVE RELAYS AND AUTOMATIC CONTROL DEVICES

This document deals with the whole of the relays and automatons installed on the high voltage transmission network. A look is also given on the production group protective relays - See appendix 7

We may distinguish between:

2 -  1 - Protective relays against short circuits

When a short circuit appears on an asset, the relays provoke the tripping of the circuit breakers framing this asset. If this function operates correctly, circuit breakers on other asses must not be tripped. In the contrary case, circuit breakers of other assets may be tripped to insure fault clearance, but in as few in number as possible.

2 - 2 -  Protective relays against abnormal situations on the network

Including:

- overload, protective relays which switch off assets crossed by steady state currents that are too high, susceptible of deteriorating them or making them dangerous;

-  protective relays against  loss of synchronism, (out - of - step relays) designed to avoid tripping alternators in power plants when one or several of them turn at a speed different from all the other alternators supplying the same network;

- load shedding protective relays, designed for restoring the production - consumption balance and thus to avoid a drop in frequency susceptible of leading to a general breakdown of the production means.

# 2 - 3 - automatic control devices

Most of the faults created by lightning on aerial assets disappear spontaneously after a few tenth of seconds after the asset has been shut down. After certain checks it is then possible to put the asset back under power. Automatic control devices are in charge of these checks.

Other devices make it possible, when several elements are shut - off , to make quickly operate again the healthy ones.

Other ones make it possible to avoid tripping by overload by using preventive manœuvres on other cells.

Finally, others are used to maintain a correct voltage in the network by acting on the transformer tap changers.

3- GénéralitIeS  ON MEASURING, METERING AND MONITORING EQIPMENT

# 3 - 1 - MEASURING

The voltages and currents present on the network cannot be used directly, so here too, measurement reducers are used. Sensors are connected to the secondary windings of these reducers, that elaborate the values necessary for running the network, namely the active power and the reactive power on the assets, and the root mean square voltage on busbars, and send them to the remote operating equipment in the form of direct currents proportional to these values

# 3 - 2 - METERING

Using the same secondary circuits, energy meters are found but only on the following cells:

. power plants

. industrial customers,

. distribution utilities belonging not to the EDF,

.cells supplying the EDF - GDF distribution centres.

They are highly accurate and doubled only when they concern  companies  external to the EDF: power plants with foreign participation, industrial customers, non nationalised utilities.

# 3 - 3 - LOCAL MONITORING

In each substation are found:

. a mimic diagram or a control console, allowing local control of the substation in case of breakdown of the remote control,

. an event recorder, where manœuvres and signalling coming from the high voltage devices and secondary equipment of each cell are printed,

. disturbance recorders, where electric values are restored when there is a fault,

.eventually fault locaters, allowing to know the position of a fault appearing on a line,

. quality meters, on customer cells, making it possible to measure the disturbances it had undergone.

# 3 - 4 - MONITORING ON THE GROUPED SWITCHING DESK ( GSD )

The GSD are control rooms in manned substations from where it is possible to exploit a set of  unmanned substations. By exploitation, we mean the maintenance of the material, and exceptionally the control of the network. To help the maintenance in the unmanned substations, it is possible, by telephone (MODEM) to obtain restitution of information present on the monitoring equipment of these substations

# 3 - 5 - Monitoring in the regional control center ( RCC )

The network is generally controlled from this point. Only the information necessary for this control is sent to it. Information concerning equipment monitoring remains in GSD.

SECOND   PART

# MEASUREMENT REDUCERS

# (by clicking above you return to the general summary)

1 - current transformers

2 - wound voltage transformers

3 - capacitive voltage transformers

4 - safety problems concerning measurement reducers

5 - commissioning

6 - optical reducers

1 - current transformer

This device is designed for feeding the protective relays and the measuring and metering equipment. The required performances are very different, depending on whether it concerns supplying a protective relay against short circuit or another equipment. The first one must receive a correct image of a current whose value may be very high and which may include a transient component, while others must receive an accurate image of a steady state current lower than, or equal to the rated current.  This is why the current transformer includes at least two windings on two distinct cores. In the following, we will only study the "protective relay" winding.

A current transformer is a system with total counteraction, and its complete study is rather complex, especially when non-linear phenomena, such as saturation and hysteresis, are taken into account. We will study a series of simplified studies, to show the origin of the constraints related in their specifications, of the errors proper to their functioning, and of their limits.

1-1- Presentation

A current transformer is a step - up transformer, the secondary winding of which is almost short - circuited.

i1					i2

secondary burden

primary winding			   secondary winding			(protections

or metering)

On the primary side, the number of turns is weak. In the case of ring type reducers, there is in fact no turn, as the primary cable crosses straight on the magnetic core, around of which the secondary circuit is wound. In the other reducers, one or two turns may be found.

# In a perfect transformer, the secondary current is linked to the primary current by:

n1

i'2  = -	      * i1			(1)

n2

while the voltage on the terminals of the secondary winding is linked to the voltage drop on the terminals of the primary winding by the inverse ratio.

n1 and n2 are respectively the numbers of turns on the primary and on the secondary windings.

note please: in the ring type reducers, it can be shown that the straight on crossing of the primary cable is equivalent to a turn.

Practically, the rated values of the primary current are situated in the range 100 A to 3000 A, and the rated secondary current is 1 A to 5 A.

1 - 2 - First approach

Let us suppose that the secondary current is the exact image of the primary current, whatever be the burden impedance of the secondary circuit.

# With this hypothesis, when the secondary circuit is open, the secondary voltage becomes infinite.

# Such an approach is of course a nonsense, but it shows qualitatively that in case of non wanted opening of the secondary circuit the voltage becomes very high (see § 4 of this chapter).

1 - 3 - Second approach

Let us suppose that the secondary current is the exact image of the primary current when the secondary circuit impedance is weak in relation with the reducer magnetic impedance. We study then the behaviour of the reducer when a short circuit occurs on the primary network.

1 - 3 - 1 - Shape of the primary current

When a short circuit appears on an overhead line, the current circulating in this line has about the shape that may be found when a reactance coil is tripped.

R1		    L1

u1

The instantaneous voltage supplied by the source is given by:

u1 = U1 * sin (t + ),  with:

U1 = peak voltage

 = pulsation, that is  2* times the frequency

 = parameter determining the value of u1 when t= 0

At the instant  t = 0  the switch is closed. The system is then described by the equation:

u1 = R1  * i1 + L1 * di1 / dt

# R1 and  L1 being the resistance and the inductance of the circuit, and i1  the instantaneous current.

After solving we find:

- t / 

i1  = I1  * [ -sin  (- ) * e      	      +  sin ( t +  - )]        (2)

aperiodic part			sinusoïdal part

with

# U1

# I1 =

# R1² + L1² * ²

1  = L1 / R1 : time constant of the high voltage network infeeding the short circuit

tg  = t1 * 

the initial condition being: i1 = 0 for t = 0.

The asymmetry is maximum for -  = -  / 2. In that case, the equation (2) becomes:

- t / 

i1  = I1  * [ - e      	      +  cos  t ]        (3)

As an example, if the network time constant is 60 ms,  = 87°, and the maximum asymmetry is obtained for  = - 3°, i. e. when the voltage is almost zero when the short circuit appears.

As an example, if the network time constant is 60 ms,  = 87°, and the maximum asymmetry is obtained for  = - 3°, i. e. when the voltage is almost zero when the short circuit appears.

# So we find following curves, obtained for I1 = 1 and U1 = 1. The time is in milliseconds..

Statistically, faults appear rather when the voltage is close to the maximum. However, the situation described her may happen, especially after a reclosing on a fault.

1 - 3 - 2 - Flux inside the reducer magnetic core

# Let us name R2 and L2 the resistance and the inductance of the reducer secondary circuit.

The voltage on the secondary circuit terminals is::

di'2

u2 = R2 * i'2 + L2 *						 L2

dt

R2

The flux inside the magnetic core of the reducer is given by:

 =    	 	u2 * dt   =    L2 * i'2   +  R2 *   		  i'2 * dt

that gives, by replacing i'2, supposed proportional to  -i1, by its value noted in the equation n° 3:

I'2			      - t / 1			          - t / 1

 = 	      * { R2 * [ 1 *  (1 - e 	    )  - sin  * t] + L2 *  * (e	        - cos *t)}	(4)



We see that the expression of the flux contains a periodic term, and an aperiodic term. In the last one, the part due to the reactance tends towards zero when the time increases, while the part due to the resistance tends towards  I'2 * R2 * 1 .

In the usual cases, this last part creates the most of the flux.

We will suppose later that the burden is purely resistive, as it is the most constraining case. The equation 4 becomes then:

- t /1

 = o * [1 * * (1 - e 	   ) - sin  * t]			by putting:

# I'2

o =	       * R2



and the flux has the following look:

# Variation of   after a fault, with maximum asymmetry and 1 = 120 ms

t (ms)

1 - 3 - 3 - Saturation

The induction in the magnetic core is proportional to the flux. When it overcomes a value Bmax, about 2 Tesla, it practically cannot increase. The magnetic core is saturated. The secondary current is quite null. The equipment using this current as input data can no more operate correctly.

The precedent calculation shows briefly that if we do not want to overcome Bmax when the current reaches its rated short circuit value , and when the asymmetry is maximum, the induction must not overcome Bmax / (t1*) when the current reaches its short circuit value, but without asymmetry.

On the next §, we no more suppose that the secondary current is the exact image of the primary current, but we draw a mock - up reducer. and we  write the equations describing its functioning in the network.

1 - 4 - Third approach

We look for a simple mock-up to represent the reducer when it is not saturated and when there is no hysteresis. More, we neglect the stray fluxes.

# Let  be the inductance belonging to a tun. A current i circulating in this turn creates a flux:

e =  * i

The current i1 circulating in the primary circuit creates a flux

1= n1*  * i1 , n1 being the number of primary turns.

The current i2 circulating in the secondary circuit creates a flux

2 = n2*  * i2 , n2 being the number of secondary turns.

# On the terminals of the secondary turns an electromotive force e appears:

# e = - n2* d 1 + 2) / dt

# If the burden is null, the electromotive force is null:	 	        1 = - 2

# Then: 	- i1 / i2 = n2 / n1 = n, 	which is the transformation ratio.

But the burden is never null. We suppose it purely resistive (see previous §). Let R2 be this burden, including the resistance of the secondary coil, the wiring and of the supplied equipment. The equation of the secondary loop is:

e = - n2 * d/ dt = R2 * i2 , with  = 1  + 2

Thus the differential equation linking the primary current to the secondary current:

(n1 * n2 * di1  / dt + n2² * di2  / dt) * = -R2 * i2                                   	 	(1)

i1 being given by the equation n° 3 of § 131.

We may also write it:	 n2² ** ( di'2  / dt -  di2  / dt)  = R2 * i2

i'2 being the secondary current of the perfect transformer, or more:

iµ + 2 * diµ / dt =  i'2 					(2)

with :		Lµ = magnetising inductance = n2² * 

2 = secondary time constant = Lµ / R2

iµ  = magnetising current = error current = i'2 - i2

We may then represent the reducer by the following mock - up:

i'1				i'2

Lµ		iµ		     R2

1 - 4 - 1 - Maximum asymmetry on the primary current

In the equation n° 2 we replace i'2 by its value found in the equation n° 3 du § 131, which corresponds to the maximum asymmetry:

-t / 1

iµ + 2 * diµ / dt =   I'2 * ( e	        - cos  * t)				(3)

The resolution of this equation gives the error current, that we call iµ1 :

1         - t/1	      1		     	 	                    1	           1               -t/2

iµ1 =  I'2* [    	     * e	     -                      * (cos *t + *2 *sin *t) - (	   - 	         ) * e     ]

1 - 2	          1 + ² * 2²				   1 - 2     1+² *2²

(4)

The flux in the magnetic core is proportional to the error current:

 = Lµ * iµ		or 	 = iµ * t2  *  / i'2

# The equation (4) gives as examples the following curves

Image of  o for 1 = 120 ms, 2 = 1 s, I'2= 20*  (  2    A, i.e. o = 11,2 * Iµ

time in ms

Image of o for 1 = 120 ms, 2 = 5 s, I'2= 20 * (  2    A, i. e.  o = 56 * Iµ

time in ms

1 - 4 - 2 - Symmetrical primary current

# We meet this situation when , i.e. 87 ° in the example described in the § 131. The voltage when     t = 0 is close to the maximum.

In that case the differential equation n°3  (§ 141) is:

iµ + 2 * diµ / dt =   I'2 * sin  * t					(6)

The resolution of this equation gives the error current, that we name  iµ2:

I'2						     - t / 2

iµ2  = 		      * (sin *t - *2 * cos *t + *2 * e     	    )	(7)

1 + ²*t2²

Image of  , for 2 = 5 seconds, I'A = 20 * (  2   A, i. e. / o = 56 * Iµ

# time in ms

1 - 4 - 3 - Enclosure when / 4

The differential equation (2) du § 14 becomes, according to the equation (2) of the § 131:

-t / 1

iµ + 2 * diµ / dt = I'2 * [- sin ( / 4) * e 	+ sin ( * t +  / 4)]

Let us put  iµ3 = ( iµ1 + iµ2) / ( 2

where iµ1 and iµ2 are the solutions of the equations (4) and (7)

iµ3 is a solution of the equation (8)

1 - 4 - 4 - Elements for the calculation of the magnetic core

The reducers are generally specified 5 P 20. The signification of this code is: the error on the secondary current must be lower than 5 % when the primary current is equal to 20 * In, In being the rated value of the load current. This maximum error can be guaranteed in steady state functioning, for the reducers of middle quality, and in  transitory functioning, for the high quality reducers.

On an other hand for each type of reducer the precision power is specified, i. e. the maximum power transmitted to the secondary circuit when the current is In. Beyond this power the precision is no more guaranteed.

Let us study as an example a reducer with a ratio of 2000 / 1, and a power precision  15 VA. That means that its secondary circuit  resistance R2, which is the sum of the input resistance of each equipment supplied and of the wiring, do not overcome 15 .

# We suppose that the core has the shape of a ring.

1 - 4 - 4 - 1 - Approximations

The time constant 2 is always much higher than 1 , which is itself much higher than 1 / . So the following approximations:

# a) asymmetric functioning (see formula (4) of § 141)

The error has a maximum value:

iµ				

=  		+

I'2 								(8)

when	 	t = 1 * Ln (2 / 1)							(9)

and then tends towards zero

# b) symmetric functioning

The error has a maximum value:

iµ / I'2 = 2 / ( * 2)								(10)

and then tends towards  1 / ( * 2)

1 - 4 - 4 - 2 - Radius of the ring

There are two types of reducers:

- the reducers without air gap.

They are sensitive to the non - linear phenomena inherent in the magnetic circuits, so as magnetisation curve non - linearity and hysteresis. But their magnetising inductance is very high, and the error due to the magnetising current is very weak. They are generally used when a good response towards the asymmetric component 	is not researched,

- the reducers with air gap.

As long as they are not saturated, their response is linear, i. e. the secondary current is linked to the primary current by the linear differential equation (2) of § 14. But their time constant is lower than the one of the preceding reducers. This yield a systematic, well known but important, error. They are used when a good response towards the asymmetric component is researched,

For each of them, we research the minimum ring radius allowing to avoid saturation, in a symmetric and a dissymmetric functioning. For that we fix a time constant value 2 so as the error of 5% specified by the standard 5P20 is not overcome:

- asymmetric functioning: formula 8 gives approximately:	 2 > 	0,120 / 0,05 = 	2,4 s

- symmetric functioning: formula 10 gives:			2 > 	2 / ( * 0,05)	= 	0,12 s

# We retain the greater value 2,4 s.

# a) Reducers without air gap.

We look for the greatest possible magnetising current before saturation:

r



the average elementary induction yielded by a turn is:

µo * µr * iµ

Be =								(11)

2 * 

with	µ r 	= 	core magnetic permeability

 	 = 	ring average radius

The total induction is:

# B = n2 * Be

It reaches the saturation value Bs = 2 Tesla for:

# Bs * 2 *

iµ = 								(12)

µo * µr * n2

The maximum current i'2 is: 	          20 *  (  2  A, then

- if the reducer must not be saturated for an asymmetric functioning

iµ <  i'2 * 1 / 2  = 1,4 A

# As an example, if µr = 10000, the minimal radius found is, thanks to the formula (12),  = 2.8 m.

- if it must be not saturated only for a symmetric functioning,

i µ = 2 * i'2 / () = 0,07 A

and, thanks to formula (12),	 =	0.14  m

The accuracy is then           0,07 / (20 *  (  2  ) = 0.25 %

The radius   can be even decreased by using reducers with a secondary rated current 5 A. The ratio n2 is then five times lower, but the needed secondary power  is more important.

# b) Reducers with air gap.

The cores of these reducers have air gaps of a few tenth of millimetres each, displayed around the ring. Let us suppose that their magnetic circuit reluctance is entirely due to the air gaps, and we research what must be their minimum value so that he induction do not overcome 2 Tesla when the primary current is maximum and the error maximum.

the average elementary induction yielded by a turn is:

Be = µo * iµ / e			e being the total length of the air gaps.

# The total induction is

B = n2 * Be = n2 * µo * iµ / e

It must be lower than 2 Tesla, then:

e > n2 * µo *  iµ / 2

- If the reducer must not be saturated for an asymmetric functioning,  	e  = 	1,8 	mm

- If the reducer must not be saturated only for a symmetric functioning,	e = 	0,09 	mm

# The minimum radius of the ring is then fixed by the minimal radius r of its section.

The magnetising inductance is, in every case:

# Lµ = 2 * R2 = 2,4 * 15 = 36  Henry

1 - 4 - 4 - 3 - Calculation of the radius r of the ring section

a) reducer without air gap

The elementary  flux yielded by a turn is (formula 11 of § 1431):

µo * µr * iµ *  * r²

e = Be * r² =

2 *  * 

The total self inducted flux by the secondary turns is:

= n2² * e = Lµ * iµ

Then, by replacing e by its value:

2 *  * Lµ		         	1	      2 * * Lµ

r = 				=	        *

n2² * µr * µo * 		n2	         µr * µo

that gives, in the example:

- If the reducer must not be saturated for an asymmetric functioning,  	r = 64 mm

- If the reducer must not be saturated only for a symmetric functioning,	r = 15 mm

b) reducer with air gap

The elementary  flux yielded by a turn is:

e = Be *  * r² =  * r² * µo * i / e

The total self inducted flux by the secondary turns is:

= n2² * e = Lµ * iµ

then: 	Lµ =  n2² *  * r² * µo / e

1	      Lµ * e

and:	r =   	       * 									(13)

n2	       * µo

- If the reducer must not be saturated for an asymmetric functioning,		r = 64 mm

- If the reducer must not be saturated only for a symmetric functioning,		r = 15 mm

So we see that if the reducers must not be saturated for an asymmetric functioning, the dimensions increase strongly.

On an other hand we see that the presence of an air gap decreases the length of the magnetic circuit, but not its section.

1 - 4 - 5 - Knee point voltage

It is the root mean square of the sinusoidal voltage which, applied on the terminals of the secondary circuit when the primary circuit is open, provoke the saturation of the magnetic circuit. More precisely, it is the value beyond which it is enough to increase it of less than 10 % to make increase the current circulating in the secondary circuit of more than 50 %.In the example studied, it has a minimum value of:

a reducer without air gap

# V knee point =  Lµ *  * Iµ =  36 * 314 * 0,0018 *20 = 405 V

b) reducer with air gap

# V knee point =  Lµ *  * Iµ =  36 * 314 * 0,05 *20  = 11,3 k V

# We see that the presence of an air gap increases the knee point voltage.

When the current runs through the reducer primary circuit and when the secondary circuit is open, the maximum voltage appearing on its terminals is approximately the same as the knee point voltage. That is the reason why the reducers with air gaps must be imperatively protected by light arresters, generally set at 2 kV (see § 41)

1-5- Usual types of current transformers

Three types of reducers can be found on the EDF network:

- reducer called "classe PS", (EDF appellation), the induction of which is at the limit of saturation in symmetric functioning (sinusoidal mode), for the maximum specified short circuit current. These device is in conformity with the IEC 185 standard. Its rated secondary current is 5 A. It has no air gap.

When it is saturated, it supplies one correct alternation out of two. It may only be used with protective relays able to send no unwanted order in these conditions. We will see further that those relays are old fashioned equipment, or models including a system making them insensible to saturation.

- reducer called "ME 21",which are half way to saturation in symmetric functioning, for the rated short circuit current. Its secondary rated load current is 5 A. It has a little air gap. Its knee point voltage is 600 V.

Thus, after a reclosing on a solid fault, if its magnetic circuit has kept a residual induction, it does not overcome the saturation induction in symmetric mode. In asymmetric functioning, the secondary current remains correct for one out of two alternations. This device is, in principle, also reserved for protective relays insensitive to saturation. In fact, tests show that the other relays may also be used for certain network conditions, to determine for each of them. We will see, in the appendix 4, how to determine if this type of reducer is convenient or not for a given relay, in a given network condition.

- reducer called "MA 102" (400 and 225 kV) and "MA 103" (90 et 63 kV), which is specified to deliver a correct answer even in case of asymmetric functioning after a reclosing or not. Its rated load current is 1 A. It meets the standard IEC 44-6, type TPY. Its knee point voltage is 6 kV.

Its behaviour for asymmetric functioning has been specified as follows:

they must not be saturated when they are run by the rated short circuit primary current, with an aperiodic component defined by  / 4 (see § 131), during a time T', then by a current null during a time tfr, then by the rated short circuit primary current, with the maximum aperiodic component, defined by  / 2, during a time t".

* 400 kV: the primary time constant is 120 ms, with t' = 155 ms, tfr = 1505 ms, t" = 200 ms

* 225 kV: the primary time constant is 120 ms, with t' = 155 ms, tfr = 1005 ms, t" = 60 ms

* 90 kV and 63 kV, on the low voltage side of the power transformers: the time constant is 180 ms, 				with t' = 175 ms, tfr = 1505 ms, t" = 395 ms

* 90 KV and 63 kV for the line cells: the time constant is 40 ms, 								with t' = 175 ms, tfr = 1505 ms, t" = 395 ms

# These devices are much bulkier and more expensive than the previous ones. They are called commonly "T.C. grosses têtes" , i.e. "big head C.T''s"

Bibliography [4],[6], [86]

2 - wound voltage tranformer

This is a real one phase transformer whose primary winding support the network voltage, and the secondary winding delivers an image voltage equal to 100 V / ( 3  when the primary voltage is equal to the rated voltage between phase and earth.

The same winding supplies the voltage to the protective relays and to the other equipment.

The difficulties met for its realisation are:

- supplying a secondary voltage with the required precision when the primary voltage is low. Indeed in this case the phenomena of hysteresis are especially sensitive. For precision devices we are led to using a magnetic circuit with air gap.

- "trapped" electrical charges during tripping and reclosing cycles. Indeed, after opening the circuit breakers of a healthy phase, this phase remains charged. A damped oscillating state appears, created by the capacity of the line and the inductance of the device. It may have a very low frequency, which provokes the saturation of its magnetic circuit. At reclosing, it then supplies a too low voltage, quite null, which can lead to incorrect functioning of the protective relays. Here too, to avoid this phenomenon, functioning with a low rated induction, using an air gap, is necessary. But this leads to a low precision power.

- Ferroresonance:

We call ferroresonance the relaxing phenomena with very low frequency, i. e. at 50 Hz or at a sub-harmonic frequency, generally 3 or 5, appearing when a saturable coil, here the transformer, is connected to a live element by a condensator. Primary voltage may then reach a dangerous value for the material.  This case is met, among others, for wound voltage transformers placed on substation busbars. (see 3rd part, § 18).

Condensator C1

wound voltage transformer

X

Condensator C2			    additional	     burden

coil

C1is the condensator parallel to the chambers of the circuit breaker

C2 represents the capacity between the busbar and the ground.

To avoid this phenomena, an additional coil, saturate when the voltage exceeds 110 V / ( 3 , is placed between the voltage transformer and the burden. Its inductance is sufficient not to deteriorate the voltage, in steady state functioning, the voltage delivered to the burden. In addition, the coil has sufficient resistance for damping the oscillatory phenomena that it may cause.

Bibliography [5], [6], [20]

3 - capacitive voltage transformer

his is an hybrid device, including a capacitive divider, formed by the condensators C1 and C2, and a transformer T. A coil L is added to tune both systems.

The same winding supplies the voltage to the protective relays and other equipment.

The skeleton diagram is:

400 kV / ( 3  or 225 kV / ( 3

C1				L

A							       B

S1

T

C2											burden

S2

coupling transformer

for power line carrier

telecommunication link

The inductance must be chosen so that, at point B, the voltage V1 is the one that would be obtained at A with an infinite load impedance.

# V1 = V* C1 / ( C1 + C2 )

We assume that the load brought back to B is purely resistive. Its value is:

R = R burden * n²               n being the transformation ratio.

This leads us, after reckoning, to the condition:

# L* * ( C 1 + C 2 ) = 1

This condition is true only if the frequency is the rated frequency of the network. For other frequencies, or for transient states, the image of the supplied voltage is erroneous. That is why these devices cannot be used for relays which do not filter transients.

However, the higher the load impedance is, (low burden) the more the precision remains good a frequencies different from the rated frequency.

Ferroresonance:

This phenomenon has not been, until to-day, observed on the capacitive voltage transformers used on the EDF network.

It seems however that this issue  has appear on other networks, and that led to develop ferroresonance suppressers.

# inductance

# burden

# resistance

# active suppresser

A circuit tuned at 50 hz is interposed between the transformer and the burden. Its impedance is very high as 50 hz, but much lower if the frequency is different, and this stops the phenomenon.

burden

Rf	  Lf		   R

passive suppresser

A spark gap is energised in case of overvoltage due to ferroresonance and so is the resistance R introduced inside the circuit. If the ferroresonance is maintained, the reactance Lf  becomes saturated and short circuits Rf. The impedance of the circuit is then modified.

# Bibliography [5], [6], [97]

4 - safety problems concerning measurement reducers

4 - 1 - Current transformers.

In normal operation, the flux created by the primary current is almost completely compensated by the flux created by the secondary current. But if the secondary winding is open, the voltage at this winding is proportional to the derivative of the primary flux and can reach very large values: several thousands of volts for class  PS or ME 21 type transformers which saturate rapidly, and several tens of thousands of volts for type MA 102 or MA 103 type transformers that do not saturate. This is why:

Any intervention on an open circuit is done by previously short circuiting the secondary circuit using a safety element called current short circuiter .

In addition, the various connections are realised with special connectors, SECURA or ENTRELEC type. Finally, for MA 102 or MA 103 type transformers, a voltage limiting device is installed.

When a reducer owns several cores, the secondary circuit of each of them is protected by one current short circuiter.

4 - 2 - Voltage transformers

When persons working on low voltage equipment of a dead cell inject into the secondary winding of a reducer an alternative voltage of several tens of volts, a voltage of several tens of kilovolts appears on the terminals of the primary winding. If other persons are working on conductors connected to them, they may be electrocuted.

It is thus imperative, before working on the primary circuit of a voltage transformer, to, separate its secondary circuit from low voltage equipment by using a safety device

A voltage transformer owns only one secondary circuit, which is then split into several parts, three generally, to supply the different equipment. The distribution is as follows:

-  automatic devices and sensors

- main protective relay

- emergency protective relay

Each circuit is protected individually, either by fuses, or by a circuit breaker. The choice of the relay may impose the type of protection (see " fuse breaking"	, §21123)

Bibliography [7], [8], [9]

5 - commissioning

5 - 1 - Identification problems

P1 and P2 are the primary terminals of the reducer. S1 and S2 are the secondary terminals.

For current transformers, the NFC 42 - 502 standard indicates that that the terminal P1 is isolated from the metallic cap surrounding the head, and P2 has the potential of this head. The potentials of the terminals P1 and S1 have the same direction.

On the EDF standardised schemes, the P2 terminal is on the line side. The IEC recommendation in reference gives no indication on this subject and many countries use  the inverse convention.

For the voltage transformers, the NFC 42-501 standard specifies that the terminal P1 is at the potential of the line and the terminal P2 is grounded. The potentials of the terminals P1 and S1 have the same direction. But the IEC recommendation gives different indications.

# It is thus important, for each country, to make inquiries on the conventions used.

# 5 - 2 - Test of commissioning

At the EDF, we perform very few tests of commissioning, on belief of the acceptance certificates of the manufacturer. We test:

- that the terminal P2 is on the busbar side,

- that the voltage limitor of the current transformer with an air gap operates well.

For this, we disconnect this limitor from the equipment, and supply it with an increasing voltage. The current must get through only if the voltage is greater than 550 V. We make then the current decrease until it gets no more through, and note its value just before.

# Bibliographie [4], [5], [6], [76]

# 6 - optical reducers

These devices are still experimental. They use the effect of electrical and magnetic fields on the light polarisation plane:

- voltage transformers use the Pokkels effect;

A polarised laser ray is circulating inside an optical fibre realised by using glass with a special quality, heavy flint, and wound in an electrical field created by the voltage. The polarisation plan of the light turns at an angle proportional to this field. An analyser and an amplifier placed at the end of the fibre make it possible o obtain an electrical signal, image of the primary voltage.

- current transformers use the Faraday effect.

In the same way, a polarised laser ray is circulating inside an optic fibre wound in an electrical field created by the primary circuit. The light polarisation plane turns at an angle proportional to the magnetic field. Treatment is then identical to the above.

These devices, other than the improvements expected on precision, bulkiness and price have the advantage of being completely free from saturation problems. Indeed the security constraints proper to measuring devices are deleted. However, they are compatible only with low input level relays. More, it does not exist, presently a standardised dialog protocol between the reducers and the equipment supplied (relays, automatic devices, sensors). This impose to order the design of the whole by the same manufacturer, and this is not accepted by the EDF..

A consensus seems however to be possible, which could lead to a standardised dialog protocol.

Bibliography [10], [11]