SEVENTH  PART

(by clicking above you return to the general summary)

MEASURING,  METERING, AND  MONITORING  EQUIPEMENT

1 - MEASURING  SENSORS

2 - ENERGY  METERS

3 - EVENT RECORDER

4 - DISTURBANCE  RECORDER

5 - FAULT  LOCATOR

6 - QUALIMETER

1 - MEASURING  SENSORS

1 - 1 - THEIR  rôle

The person operating on the network must know at any time, flowing through each asset:

- the active power P,

- the reactive power Q ,

as well as, on each substation busbar:

- the voltage,

- the frequency.

So as these data are available at the control centre, a sensor and a transfer path are necessary:

sensor		remote terminal 			data acquisition

unit				      computer

visualisation and

processing

high voltage 	   		relay		      substation			       control

cell  			building	      	control building 	     		        centre

The sensors, located inside the substation relay building, acquire the instantaneous voltages and currents on the secondary terminals of the reducers ("measurement" terminals for the currents).  Each of them deliver a direct current proportional to the data (r.m.s voltage, average power, frequency)  it has elaborated from its input data. This current is then transformed into digital signals in the remote terminal unit, then sent through a telecommunication channel to the acquisition computer located inside the control centre. The data thus sent are then visualised, and used as input data in calculation programs aimed to help the operators.

1-2- PrincipLe of power sensors

They use the "time delay modulation" method. The principle is the following::

a voltage proportional to the instantaneous current - i, to which is added a voltage proportional to a fixed reference current im, is applied on an integrator. At its input, we gather a voltage of the form k *  (im - i) * dt. At the end of a time T1, this voltage reaches a given threshold S. An electronic switch (chopper) then replaces  - i   by  + i on the input of the integrator. The output voltage goes back to zero at the end of a time T2. The switch then goes back to its initial position. We have:

T1	                 T1 + T2

S = k *    (im - i) * dt  = k *    ( im + i) * dt

0	                  T1

thus:

T1 + T2

im *  (T1 - T2) =       i * dt

0

If the time lag  T1 + T2 is small in relation with the period 20 ms of the current i, we admit that i has not varied during this time, and we find:

T1 - T2

i  =  im  *

T1 + T2

The period T1 + T2 depends on the value of i. It is minimal for i = 0. It is about 0.2 to 0.5 ms. The current i must always remain lower than im.

resistor

-i

chop per

+i

amplifier

im									s

+v

instantaneous power                  			average

-v			P						power

During the same period, the instantaneous voltage v is applied on the input of an electronic switch synchronous with the preceding. On the output we find a voltage equal to + v for the time T1, and - v for the time T2. If we admit that v has not varied during this time,  the average value of the voltage at point P during the time T1 + T2  is then:

T1 - T2	         	 i

v  *		               =  v *

T1 + T2	        	1m

value proportional to the instantaneous power.

The voltage obtained after the switch is then sent to an integrator, which deliver a direct current proportional to the average power, in a range from 0 to 10 mA if they elaborate a value which is always positive, from - 5 mA to + 5 mA in the contrary case.

s

T1	 	  T2							           t

1 -3 - Différent types of  sensors using the principle  described  above

1-3-1- Active power sensors for unbalanced three - phase  networks

Three modules are necessary, each of them measuring the active power of each phase. A common summing integrator delivers the current proportional to the sum of the three powers.

P = Vr * Ir * cos jr + Vy * Iy * cosjy + Vb * Ib * cosjb

1-3-2 Active power sensors for balanced three - phase  networks

It measures the active power on a single phase

P = 3 * Vr * Ir * cosjr

1-3-3- Reactive power sensors for unbalanced three - phase  networks.

Three modules are necesary, but on each of them the current of a phase is associated with the voltage meaured between the two other phases..

Q = (Uyb * Ir * cosjr + Ubr * Iy * cosjy + Ury * I b* cosjb) /    3

1-3-4- Reactive power sensors for balanced three - phase  networks.

Three methods are possible:

- use of a module of the preceding sensor

Q =    3  * Uyb * Ir

- use of an active power sensor with a condensator on one of the two input data, to phase shift it by 90 °.

Q =  3 * Vr * Ir * sinjr

- use of a module olicited by the current difference Ir - Ib

Q =  3  * (Ir - Ib) * Vy

1-3-5- Voltage sensors

The voltage is applied on both inputs. The output current is proportional to the square of the r.m.s voltage.

1 - 4 - Choice of the sensors.

For a given enor, the maximal input values are fixed. A sensor thus must not be set but chosen. Modification of the maximal possible load of a line, or of the ratio of a current transformer, can lead to replace it. Thus the interest of installing these sensors on plug - in bases.

1 - 5 - frequency sensors

The voltage of the network is put into the form of square signals whose width is compared to 10 m signals started by the pasage through ero of the voltage. The deviation is sent to an integrator, on the output of which we find a positve or negative direct current, proportional to the deviation of the frequency with respect to 50 Hz.

- frequency lower than 50 hz

grid voltage

A

B									10 ms square signals

_

A * B									deviations (f <50 hz)

_

A * B									deviations (f >50 hz)

- frequency higher than 50 hz

grid voltage

A

B										  10 ms square signals

_										 deviations (f < 50 hz)

A * B

_										 deviations (f > 50 hz)

A * B

Bibliography [62], [63], [128]

2 - energy meters

Metering installations on the high voltage transmission network concern:

- industrial customers supplied directly by the 400 kV, 225 kV, 90 kV, and 63 kV networks,

- the generation plants,

- points of supply to electricity distribution utilities which are not a part of the EDF,

- points of supply to EDF distribution centres (power transformers 225 kV / 20 kV, 90 kV / 20 kV, or 63 kV / 20 kV.

2 - 1 - Metering  installations of the most important customers.

They are designed in order to obtain the best compromise possible between EDF constraints and cutomer wishes.

2-1-1- EDF constraints:

- to invoice the customer for the energy he consume at a price taking into account the marginal Kwh cost.

- to invoice line losses due to the reactive energy consumer's consumption,

- to ensure an accurate, reliable and fast invoicing,

- to have the possibility of rapidly decreasing the consumption in case of difficult situation on the network

- to gather statistical data useful for planning its investments.

2-1-2- Customer's wishes:

- to know in advance the cost that will be invoiced to him in kwh in order to optimise his load plan,

- to know his active and reactive energy consumption in order to be able to avoid overcosts,

- to be forewarned of voluntary EDF cut - offs (the accidental cut - offs are treated in the ninth part).

2-1-3- Example of agreement.

his is a "very high consumption day erasure " type agreement.

There are, in this example, five tariff periods, classified in the order of decreasing tariffs:

- tariff n°1, called   " very high consumption day ".

There are a maximum of 22 very high consumption days, chosen among the working days in November, December, January and February. During these days, the tariff n° 1 may be applied for a maximum of four hours, at periods of the day specified in the agreement. These day are chosen by the EDF, the day before for the next day. The tariff practised are dissuasive and make it possible to avoid setting up costly generation means for the EDF, inciting the customer to reduce his consumption or to supply himself by independent means.

- tariff n°2, called "winter high consumption hours"

This tariff i applicable from 6:00 a.m. to 10:00 p.m., every working day inside the period from October 1 to march 31.

- tariff n°3, called "summer high consumption hours"

This tariff applies to the same hour, the other months of the year.

- tariff n°4, called " winter low consumption hours"

- tariff n°5,called "summer low consumption hours"

The subscribed power i a function of the tariff period. It is higher during the low consumption period than during the high consumption period. Overshooting is authorised exceptionally. They are invoiced.

If the reactive energy exceeds 60% of the active energy during high and very high consumption hours, overshooting is invoiced.

To manage such agreement, the system called " stage 90 metering system" was set up.

2-1-4- General archiecture of the stage 90 metering system.

Console of the national			  national			console for        national

sales service			  computer			statistique          level

(Clamart)

telecommunication

network

console of the control			metering		           synchronised       regional

centre						           	                 clock              level

management

(Nancy for example)

computer

consoles of the regional

sale service, for statistical

and technical application

telecommunication

network

local				niveau client

controller

metering				          metering

cabinet				          cabinet

2-1-4-1- Function of the metering management computer

- It acquires:

.  from the console of the national sale service, and through the national computer, the tariff rule to be applied,

. from the console of the regional sales service, the invoicing rules foreseen in each of the EDF - customer agreements,

. from the console of the control centre, the random tariff orders authorised by the EDF -customer agreements, such a the choice of very high consumption day,

. from a clock synchronised on a national emitter, the exact time, which it distribute to all the local controllers,

. from the local controllers, the information necessary for invoicing: the energy consumed for each tariff period, i. e. the active power, the reactive power, the average active power for each period of 10 minutes.

- It reckons the invoices and sends them to the invoicing service.

- It end to the local controller the information foresee by the agreement and allowing the customer, on one hand, to adapt himself to random tariff orders emitted by the control centre and, on the other hand, to check hi invoices: statement of active and reactive power, energy overcoming, active and reactive power consumption, and, if relevant, energy supply to the EDF.

2-1-4-2- Function of the local controller.

- It acquires the information coming from the meters, calculates the amounts due with respect to the agreement, and sends them to the metering management computer.

- It elaborates the documents foreseen by the agreement, allowing the customer to optimise hi electric consumption. these are mainly the load curves.

- It sends to the customer information coming from the metering management computer and foreseen by the agreement.

- It orders, if the customer o wishes, automatic flip-flops linked to tariff conditions in his installations.

2-1-4-3-Meters

A supply point may include one or several terminals. Are found on each of them:

- a watt - hour meter, of class  0.5  S or 0.2  S , the letter S meaning that they meet the standard relative to static meters,

- a class 3 var - hour meter

- a class 1 single phase meter, on each phase.

2-1-5- Functioning of the meters

The static meters have the same measuring element as the power sensor (see § 1). The output signal, proportional to the power, is then integrated until it reaches a given level, corresponding to a given amount of energy. The meter then sends a pulse and the integrator is reset to zero.

The electromechanical meters use the ferraris disk principle, described in the chapter devoted to electromechanical protective relays (see third part, § 2123).

The local controller acquires these pulses and reckons, from its tariff tables, the price of the energy to be invoiced to the customer. Invoicing is basically performed from an active three - phase meter, which is a static meter.

The var - hour meter, which is electromechanical, is used to invoice energy overshooting during high or very high consumption periods.

The single phase meters, which are electromechanical, are not connected to the local controller. They are only used locally to check the good operation of the system. Indeed, all five meters have one or several digital displays that may be compared amongst themselves.

2 - 2 - supply  to  other  customers.

A local controller having all the performance described above is not always necessary, especially for customers whose installed power is relatively low. This is why a simplified version has been developed.

2 - 3 - international  links  and  power  plants  with  foreign  participation.

From various generation sites and various ends of international links, the sensors end their measurements to the regional control centre. Here, the measurements are integrated to obtain the amount of energy necessary for international invoicing operations, and sent to Laufenburg (Switzerland), where energy exchange invoicing is performed.

These acquisition channels are doubled by meters installed on various site, and which send their results directly to Laufenburg.

2 - 4 - supply of electricity utilities.

The points of supply are treated like the ones of important customers

2 - 5 - supply of distribution  Centres belonging to the edf

Each 20 kV end has a class 0.2 three phase watt - hour meter, two class 3 three phase reactive meters, one in each direction, and a remote reading power recorder, which is in fact a simplified local controller. It functions are:

- acquisition of pulses sent by the meter at each end,

- establishment of invoices internal to the EDF,

- establishment of average power tables per 10 minutes: active power, absorbed reactive power, repressed reactive power.

This type of metering is also installed on the terminal supplying the French railroad (Société Nationale des Chemins de fer Français).

Bibliography [64], [65]

3 - the  event  recorder

3 - 1 - its  rôle.

Its role is to acquire data, as position of gears, orders from protective relays, or indications of failure, susceptible of appearing in the cells, and to restore them in a readable form with, for each of them, the exact time of its appearance and disappearance, within 10 milliseconds.

This allows the operator, if an anomaly appears, to make a decision making it possible to continue, or to restore, the operation of the part of the network that could be affected. This also make it possible, subsequently, in case of important incident, to analyse accurately what has happened.

Restitution takes place, as the data arrive, on a printer located near the recorder.

It may also be performed from a distance, on call by a modem using the public telephone network, from a console.

In a substation, some data must be followed by an immediate action. To do this, they set off a sound alarm. The event recorder elaborates this alarm, but the EDF does not use this possibility since this function is elaborated in an other equipment.

note: the event recorder function can be installed in the same equipment as the remote terminal unit.

3 - 2 - Example  of  equipement.

Let us consider the PAS 692 from Techniphone.

- It is supplied in 48 V direct current in order to be able to operate on secondary batteries in case of auxiliary supply failure.

- It may be connected to an external clock, synchronised on a national emitter (France Inter).

- It may acquire the data of 16 cells, at the rate of 32 simple data per cell. This is a small capacity computer.

- Each data is sent to the printer in the form of a 64 character line, including:

. 8 characters for the time,

. 16 characters for the name of the bay and of the substation,

. 32 character for the description. For example “ trip first step relay PX ” ,

. 6 character for the status of the order emitted or the position of the monitored device. For example, for a circuit breaker, “ open ” or “ closed ” and for a tripping order emitted by the relay, “ begin ” or “ end ”.

The configuration, i. e. the text corresponding to each data, may be performed either directly on the recorder, or on an external configurator. The second possibility makes it possible, when the substation structure changes, to prepare the new memory board and to install it quickly on the event recorder, without interrupting substation operation. It also makes it possible to keep a copy of the configuration in case of recorder failure. The recorder can store until 2000 records.

3 - 3 - operating  problems

The main problem is the discrimination of operating data from data appearing during test. Indeed, a series of tests on a bay provokes the appearance of a number of data as great as the number of data appearing in normal operation for several months. So, if you do not pay attention to them, the outstanding data are drowned in the middle of data with lesser importance. It is thus important to be able to pick out the bay which is being tested in order to route these data on a printer different from the operation printer.

3 - 4 - Place of the event recorder in the control of the network: see eighth part, § 4

Bibliography [66], [67], [68]

4 - the  disturbance  recorder

4 - 1 - its  rôle.

The event recorder described above is generally not enough to analyze incidents correctly. Indeed, this equipment only give information in the form of “true” or  “false”  signal, and it  is often necessary to know the evolution of the form of voltages and current during a fault.

4 - 2 - its  functions.

- To record permanently the shape of the current and voltage waves, with a sufficient dynamic to distinguish the fault currents from normal operation currents, if they are effectively different,

- to record in the same time a few data which can be also found on the event recorder, and that might influence the voltage and the current waves,

- to keep in memory these recordings for a few hundreds of milliseconds,

- to restitute them on the printer, when it is solicited by a significant incident signal, as for example the pick up of a protective relay. Recordings done just before the incident are, of course, part of the restitution since this is the basic interest of the device. Restitution last a few seconds, and may be reinitialised by a new solicitation, for example a reclosing order signal.

- to keep in memory the locally restituted data in order to be able to obtain their remote restitution, like the event recorder,

- to be, like the event recorder, connected to a synchronised clock, generally the same one, in order to make an easy correlation of the respective restitutions.

4 - 3 - Example of  disturbance recorder

Let us consider the  TPE 2000 of GEC-Alsthom. This is a system which includes:

- an acquisition unit  for two bays, capable of recording 8 analogical values, voltages and currents, and 16 true or false data. The acquisition of analogical values is performed by sampling, 32 samples per period, and the digitalisation of each sample is done on 12 bits.

Memorisation, adjustable from 200 to 500 ms, is set to 200 ms in the EDF substations.

The restitution duration, adjustable from 0.1 sec to 25 sec, is set to 3 sec in the EDF substations.

This unit can restitute its acquisitions by sending them immediately to a nearby restitution unit by a RS 232 link or a current loop;

- a restitution unit per substation. It is installed in the control building and receives the recordings of the acquisition units of the substation. It has  it own clock  which can be synchronised by an external clock. It restitutes its information onto, a printer and can be interrogated from a distance by an external console, through the public telephone network, by using a modem;

- an external console , eventually. It is completed from a personal computer. It may interrogate the restitution units.

In small substations, where a single acquisition unit is enough, the restitution unit may not be installed. In this case, the acquisition unit transcribes its recordings on a floppy disk which can be read on a restitution unit located on another site. It may also transfer, through the public telephone network, its information to an external console. The dating of the registered data can be found by observing the registered voltages.

Bibliography [69], [70]

5 - fault  locator

5 - 1 - its  rôle.

To measure, from the voltages and currents of a cell, the reactance of a line segment located between the close end and the site of a short circuit. This reactance being proportional to the distance, the site of the fault can then be determined.

This device allows the operator to locate rapidly, in terrain which is difficult to reach, forced outages such as cable rupture, line sleeve rupture or tower ruin. It may also be useful, in case of intermittent fault, to show weak points such as badly pruned trees, polluted insulators, ...

5 - 2 - its principle.

It must acquire and memorise data allowing it to measure the reactance during the time separating the appearance of the fault and its clearance, that is less than 100 m in most cases. It must thus adapt itself to, a possible slow transient state, such as the ones obtained at closing a reactor.

For this, it uses the same data as the ones that were seen for the distance protective relays (see third part,  § 213), for the determination of the first zone. However, instead of comparing the signs of the compensated voltages when the pilot go through zero, it memorises, at that instant, the line voltage and the image voltage, then subsequently, makes it the ratio.

Let us name x this ratio. If the image voltage is obtained with the resistance and the reactance of the whole line, the ratio x is the distance of the fault, in percentage of the line length. Indeed, for a phase to earth loop, for example, the phase to earth voltage is:

d

v = [ R * (ir + ko * ig) + L *        ( ir + ko * ig ) ] * x + Rd * ig

dt

and we elaborate

d                                                       (1)

v image = R * ( ir + ko * ig) + L *       ( ir + ko * ig)

dt

R, L, and Rd being respectively the line resistance, its inductance, and the resistance of the fault.

For ig = 0, the instantaneous voltages become:

v' = ( R * ir + L * dir / dt) * x                                                                                                                      		v' image = R * ir + L * dir / dt			thus:      		v' =  x * v' image

We note, moreover, that the device has a phase selector with principle similar to the one of the PDS, and a zero sequence compensation with principle similar to the one described in the § 2127 of the third part.

The fault locator of the same substation send their information to a restitution unit located in the substation by RS 232 link or a current loop. This restitution unit may be interrogated from a distance.

Bibliography [71]

6 - QUALITY METER

The aim of this device is the analysis of the data noted in the agreement "Emeraude", so as to characterise the energy supply quality (see 9th part, § 5), i. e. :

- voltage drops and short outages,

- imbalance rates,

- harmonics,

-flicker.

It is installed on the supply points from the high voltage network to the industrial customers or to the distribution utilities.

It acquires

- the three phasor voltages and the residual voltage,

- the three phasor current and the residual current.

It works out the data to be returned by two ways:

- the "cyclic" mode: the device reckon, during a given time, 100 s for example, the considered data, and stores it in a memory. This mode i used to observe the behaviour of the electric data of the end when it operates without disturbance;

- the "threshold" mode: when a data crosses a threshold, the device notes the time of threshold crossing, and the mean value of the data until it crosses another threshold, or the same threshold in the opposite sense. When a data has again a normal value, the mode is disabled. This mode is designed for observing the disturbed working of the network.

These data are::

- the 4  r.m.s. voltages.

their observation according to the "threshold" mode gives the voltage drop and the short, or long, outages. Seven threshold are available, so as to characterise the depth of the drop,

- the 4  r.m.s. currents,

- the frequency,

- the active power on each phase,

- the reactive power on each phase,

- the power factor on each phase,

- the harmonic rate, for each chosen row, from the row 2 to the row 50, on the voltage and current of each phase,

- the global distortion ratio on the voltage and the current of each phase,

- the imbalance ratio,

- the presence of 175 Hz and 188 Hz signals, greater than a given level (0.5 * Un).

These values can be read on the front face of the device. They may also be stored in a memory, to be read by a close or remote terminal unit.

Note: an issue which often appears between the EDF and its customers is to know, in case of abnormal harmonic level, where the source of harmonics is:

by the customer or on the network?

To determine it, it is necessary to install several qualimeters. The one which shows the highest value is the one which is located on the source of harmonics.

network

3

substation

1	2

customer n° 1		customer n° 2

If the harmonic rate given by the qualimeter located on the end 1 is greater than those given by the other qualimeters, the main source of harmonics is the customer n° 1.

Bibliography [72], [73]