APPENDIX  3

(by clicking above you return to the general summary)

ELECTRICAL  CHARACTERISTICS OF THE  LINES

1 - Matrix of the inductance values								3

1 - 1 - Preliminaries:  inductance per length unit of a double wire line				3

1 - 2 - Single circuit three phase line, one wire per phase, perfectly conductive soil, no earth cable.	4

1 - 3 - Single circuit three phase line, one wire per phase, resistive soil, no earth cable.			6

1 - 4 - Single circuit three phase line, several wires per phase, resistive soil, no earth cable.		6

1 - 5 - Double circuit three phase line, several wires per phase, resistive soil, no earth cable.		6

1 - 6 - Single circuit three phase line, one wire per phase, resistive soil, one earth cable.		8

1 - 7 - Double circuit three phase line, several wires per phase, resistive soil, two earth cables.		11

2 - Matrix of the capacitance									14

3 - Matrix of the resistance									14

4 - Matrix of the transverse conductance								14

ELECTRICAL  CHARACTERISTICS OF THE  LINES

we try to determine the characteristics of the electrical lines, as they are defined by the matrix equation seen at  § 21 of the appendix 1.

1 - Inductance matrix

1 - 1 - Preliminaries: inductance per metre  of a double wire line

The formula given in the  Techniques de l'Ingénieur, Vol D1, page 69-8, formula 613, [89], is:

µo	      µr			D

L = 		* (	    +  Log 	       )			Log = Napier logarithm

2*	       4			r

with:		µr 	= 	magnetic permeability of the wires, here equal to 1,

D 	=	distance between each wire, in metre

r 	= 	radius of each wire, in metre

L 	=	inductance per metre, in henry / m

µo 	= 	4 *  * 10-7

The term  µr / 4 corresponds to the internal inductance, i. e. created by the flux inside each wire, and the term Log ( D / r) corresponds to the external inductance i. e. created by the flux outside the wires.

This formula does not take into account the kin effect, which increases the density of the current near the surface of the wires, and decreases the term µr / 4. In fact, in the calculations of the energy transmission lines, this term is neglected. It remains:

µo		D

L =	      *	Log		 							(1)

2*		r

In the infinitely short line element beneath, the instantaneous values v and i are linked by:

d (va - vb)		di

- 	          =	L *

dx			dt

i

i			           r

dx

1- 2 - Single circuit three phase line, one wire per phase, perfectly conductive soil, no earth cable

The soil is thus considered as a mirror in which the conductors are reflected. The currents in the reflected conductors run in the sense opposite to the real conductors.

vy

y

iy

vr

r

ir		dry	            vb

b

ib

hr		 hy		   hb

dyb

- vb

b'

- vr			         - ib

r'

- ir

- vy

y'

- ib

figure 1

If the conductor r is run by the current  ir = i and the conductor  y by the current iy =  -i,

the equation 1 becomes:

d(vr - vy)		Lry	       d (ir - iy)

-  		  =  		* 						(2)

dx		 	2	             dt

This equation can be generalised to the case where ir is different from - iy. We consider that the current iy  make a voltage drop on vr, and that the current  ir make a voltage drop on vy:

dvr / dx = (Lry / 2) * diy / dt

dvy / dx = (Lry / 2) * dir / dt

Thus the equation giving the voltage drop on vr:

Dvr     µo	       Dry      diy	           Drb      dib           Drr     dir            Dry'     diy	Drb'    dib

=	       * (Log 	  *        +  Log	      * 	  - Log	      *	  - Log	      *	    - Log         *        )

dx       2 *	         r	      dt		  r          dt           r         dt	  r        dt                 r       dt

in which Dry, Drb.. are the distances between the conductor r and the conductor y, between the conductor r and the conductor b, ...

The equations giving the voltage drop on  vy and vb are deduced from the equation above by circular permutation. Thus, after simplification, the equation giving the matrix of the inductance:

dvr				Drr'			Dry'			Drb'

Log		    	Log 			Log			ir

dx			 	   r			 Dry			 Drb

dvy	    µo			Dyr'			Dyy'			Dyb'	   d

-	=	  *	Log			Log			Log	            *   	iy

dx        2*		     	Dyr			   r			Dyb	   dt

dvb				Dbr'			Dby'			Dbb'

Log			Log			Log			ib

dx				Dbr			Dby			   r

inductance matrix				(3)

From figure 1, we find:

Drr' = 2 * hr		Dry'² = (hr + hy)² + dry²		Dry² = (hr - hy)² + dry²

Dyy' = 2 * hy		Drb'² = (hr + hb)² + drb²		Drb² = (hr - hb)² + drb²

Dbb' = 2 * hb		Dyb'² = (hy +hb)²  + dyb²		Dyb² = (hy - hb)² + dyb²

The inductance matrix can be diagonalised by the symmetric component if the terms of the diagonal are equal and so do also the other term. To use these component, the currents and voltages must be complex variables. The values taken for h and d are mean values, i. e.:

h = (hr * hy * hb) 1 / 3		d = (dry * dyb * dbr) 1 / 3

The terms located on the diagonal have following value:

µo 		     2*h

L =   		 *  Log

2 * 	  	       r

and the other terms:

µo 		      	4*h² + d²

M =		       *	   Log

4 * 	  	          	    d²

The eigenvalues are then:

µo 			2*h 		   4 * h² + d²

Ld = Li  = L - M =   		 *  (2 * Log 		   -  Log		         )

4 * 	  	  	   r		          d²

µo 		              2*h 		    4*h² + d²

Lo = L + 2 * M  =   		*   (      Log 		   +  Log		        )

2 * 	  	                r		         d²

The heights which are used are the mean heights, obtained from the mean H between the anchoring points and the arrow F by the formula:

h = H - 2 * F / 3

The arrow is given by the approximate formula:	 	F = P * (   P² + H²   / (8 *a)

with:	P =  	horizontal range

H = difference in level between both anchoring points

a = parameter for installing the line (linked to the mechanical tension)

This formula is found in the Techniques de l'Ingénieur, Vol D41, page D 4421, formula 14. [89]

1- 3 - Single circuit three phase line, one wire per phase, resistive soil, no earth cable.

We can use the same formulae as previously ( § 12), but we must place the mirror no more at the surface of the soil, but at a depth  given by:

 =(µo * 

with:	 = soil conductibility , in mho/m

 = 100 * 

The equations (4) become then :	Drr' = 2 * (hr + )		Dry'² = (hr + hy + 2*)² + dry²						...					...

...					...	(5)

1- 4 - Single circuit three phase line, several wires per phase, resistive soil, no earth cable..

If each conductor is formed of n identical wires (n = 2; 3; 4) the preceding reckoning remains relevant by replacing the radius r of the conductor by an equivalent radius req given by:

1 / n					          r

req = 	(r * R n-1 )

R

n = 4

1- 5 - Double circuit three phase line, several wires per phase, resistive soil, no earth cable.

The matrix (3) becomes then a 6 * 6 matrix, in which the index 1 is given to the parameters concerning the circuit n° 1, and the index 2 to the parameters concerning the circuit n° 2.

dvr1	               Dr1r'1	        Dr1y'1	   Dr1b'1           Dr1r'2	     Dr1y'2	  Dr1b'2

Log	Log	         Log 	   Log	           Log	      Log		 	 ir1

dx	               req	        Dr1y1	   Dr1b1	           Dr1r2	     Dr1y2	  Dr1b2

dvy1	               Dy1r'1	        Dy1y'1	   Dy1b'1           Dy1r'2	     Dy1y'2	  Dy1b'2

Log	Log	         Log	   Log	           Log	      Log			iy1

dx	               Dy1r1	         req	   Dy1b1	           Dy1r2	     Dy1y2	  Dy1b2

dvb1	               Db1r'1	        Db1y'1	   Db1b'1           Db1r'2	     Db1y'2	  Db1b'2

Log	Log	         Log	   Log	           Log	      Log		 	ib1

dx        µo	 Db1r1	        Db1y1              req	           Db1r2	     Db1y2	  Db1b2 	     d

-          =	      *										 *

2*	 									     dt

dvr2		 Dr2r'1	       Dr2y'1	   Dr2b'1           Dr2r'2	     Dr2y'2	 Dr2b'2

Log	Log	        Log	  Log	           Log	      Log			 ir2

dx		 Dr2r1	       Dr2y1	   Dr2b1		  req	     Dr2y2	 Dr2b2

dvy2		 Dy2r'1	       Dy2y'1	   Dy2b'1           Dy2r'2	     Dy2y'2	 Dy2b'2

Log	Log	        Log	  Log	          Log	     Log			 iy2

dx		 Dy2r1	       Dy2y1	   Dy2b1	           Dy2r2	        req		 Dy2b2

dvb2		 Db2r'1	       Db2y'1	   Db2b'1           Db2r'2	     Db2y'2	 Db2b'2

Log	Log	         Log	   Log	           Log	      Log			 ib2

dx		 Db2r1	       Db2y1	   Db2b1	           Db2r2	     Db2y2	    req

If the terms written in blue are equal each other, and if among the other terms the ones written in red are equal  each other, the symmetric components of the voltages and the currents are linked between each other by the following equations:

dVd1   	   					dVd2

=  j *  * Ld1 * Id1 	   		            	=  j *  * Ld2 * Id2

dx	     					  dx

dVi1   	   					dVi2

=  j *  * Ld1 * Ii1 	   		            	=  j *  * Ld2 * Ii2

dx	     					  dx

dVo1   	   					dVo2

=  j *  * (Lo1 * Io1 + Mo * Io2) 	   	=  j *  * (Lo2 * Io2 + Mo * Io1)

dx	     					  dx

by putting:

µo 		       2*h1 	      	4 * h1² + d1²

Ld1 = Li1  = L1 - M1  =   		*  (2 * Log 	      -        Log		        )

4 * 	  	         req		     d1²

µo 		       2*h1 		4*h1² + d1²

Lo1 = L 2+ 2 * M2     =   		 * (2 * Log 	      + 2 *  Log		        )

4 * 	  	        req			     d1²

µo 		        2*h2 		 4 * h2² + d2²

Ld2 = Li2  = L2 - M2 =   		*  (2 * Log 	       -  	    Log		           )

4 * 	  	         req		       d2²

µo 		        2*h2 		    4*h2² + d2²

Lo2 = L2 + 2 * M2     =   		 * (2 * Log 	        + 2 * Log		             )

4 * 	  	          req		         d2²

µo 		     4*h12² + d12²

Mo = 		 		 * Log			    )

4 * 	  	    	d12²

with:

h1 = (hr1*hy1*hb1)1/3  + 			d1 = (dr1y1*dy1b1*db1r1)1/3

h2 = (hr2*hy2*hb2)1/3  + 			d2 = (dr2y2*dy2b2*db2r2)1/3

h12 = (hr1*hy1*hb1*hr2*hy2*hb2)1/6  + 		d12 = (dr1y1*dy1b1*db1r1*dr2y2*dy2b2*db2r2)1/6

1- 6 - Single circuit three phase line, one wire per phase, resistive soil, one earth cable.

Let us consider again the figure 1 du § 11, in which the earth cable is added, and also its image in the mirror.

Vg = 0

g

ig

vy

y

iy

vr

r

ir		dry	            vb

b

ib

hr		 hy		   hb

dyb

- vb

b'

- va			         - ib

a'

- ia

- vy

y'

- iy

-vg = 0

g'

- ig

The equation giving the voltage drop on vr is:

dvr	   µo	            Dry     diy	 	Drb     dib	    Drr'      dir	      Dry'     diy	        Drb'    dib

=	          * (Log 	      * 	   + Log	         * 	     - Log            *         - Log	  *        - Log         *

dx	 2 *	             r          dt	    	   r        dt                   r	   dt	          r	      dt	           r	     dt

Drg    dig	  	   Drg'	  dig

+ Log	     *	   - Log	           *	          )

r        dt		     r	   dt

in  which Dry, Drb.. are the distances between the conductor r and the conductor y, between the conductor r and the conductor b, ...

More, the voltage drop on the earth cable is null:

Dvg     µo	      Dgr       dir	     	Dgy     diy	   Dgb    dib	   Dgg'      dig	     Dgr'    dir

=	      * (Log 	  * 	  +  Log	        * 	    + Log	          *	      - Log           *         - Log         *

dx       2 *	         r	      dt		     r      dt                 r	dt	        r	    dt	         r	    dt

Dgy'	diy	            Dgb'	dib

- Log	       *		- Log	       *	       ) = 0			(2)

r	dt		 r	dt

The equation (2) allows to eliminate in the equation (1) the term Ig. That equation becomes:

dvr	   µo	         	Drr'		Drg'		Log ( Dg'g / Drg)		dir

=	           * [ (Log	         -	Log 		*			      ) *  		+

dx	  2*	        	r		Drg		Log ( Dgg' / r)	 	dt

Dry'		Drg'		Log (Dg'g / Dyg)		 diy

(Log		- Log		*			        ) *		  +

Dry		Drg		Log ( Dg'g / r)		  dt

Drb'		Drg'		Log (Dg'g / Dyb)		 dib

(Log		- Log		*			         ) *		  ](3)

Drb		Drg		Log ( Dg'g / r)		  dt

The equations giving the voltage drop on vy and vb are deducted from the equation above by circular permutation.

From figure 1 of this §, we find:

Drr' = 2 * (hr+)		Dry'² = (hr + hy + 2*)² + dry²		Dry² = (hr - hy)² + dry²

Dyy' = 2 * (hy+)	Drb'² = (hr + hb + 2*))² + drb²		Drb² = (hr - hb)² + drb²

Dbb' = 2 * (hb+)	Dyb'² = (hy +hb + 2*)²  + dyb²		Dyb² = (hy - hb)² + dyb²

Dgg' = 2 * (hg+)	Drg'² = (hr + hg + 2*)² + drg²		Drg² = (hr - hg)² + drg²

Dyg'² = (hy + hg + 2*)² + dyg²		Dyg² = (hy - hg)² + dyg²

Dbg'² = (hb + hg + 2*)² + dbg²		Dbg² = (hb - hg)² + dbg²

(4)

The inductance matrix can be diagonalised by the symmetric component if the terms of the diagonal are equal and so do the other terms. We use for the parameters h and d the average values, i. e.:

h = (hr * hy * hb) 1 / 3	d = (dry * dyb * dbr) 1 / 3	    dg = (drg * dyg * dbg) 1 / 3		(5)

The terms located on the diagonal have the following value:

µo 	      2*(h + ) 	        4*(h+hg +2*)²	Log {2*(hg+) / [(h-hg)²+dg²]1/2}

L =   	   * (2*Log 	          - Log		        *		  			)

4 * 	             r	         (h - hg)² + dg²                  Log [2*(hg+) / r]

(6)

and the other terms:

µo 	   4*(h+)² + d²	           4*(h+hg +2*)²	 Log {2*(hg+) / [(h-hg)²+dg²]1/2}

M =	   * (Log		             - Log		           *		 			)

4 * 	          d²			(h - hg)² + dg²            Log [2*(hg+) / r]

(7)

The eigenvalues become then:

µo 	                 2*(h + )	    4*(h+)² + d²

Ld  = Li = L - M =   	* (2 *Log	       - Log		 )		(8)

4 * 	  	           r		               d²

Lo = L + 2 * M

note: In the equation (2), we did not take into account the resistance per length unit  rg of the earth cable. If we want to do it, we must use the complex values of the voltages and currents, and not the instantaneous values. Indeed, the equation (2) becomes:

dvg       j**µo	  	 Dgr     	      	Dgy     	            Dgb    	          Dgg'     	           Dgr'

=	         	  * (Log 	        * Ir  +  Log	        * Iy + Log	       * Ib	 - Log	      * Ig	  - Log         * Ir

dx	2 *	  	   r	      	   r	       	   r	             r	      	  r

Dgy'	           Dgb'

- Log	       * Iy - Log	      * Ib	)  + rg * Ig = 0			(9)

r	               r

The current is split between the soil and the cable in a complex report.

In the equations (6) and (7), the term

Log [2*(hg+) / r]

must be replaced by:

Log [2 * (hg + ) / r] + 2 *  * rg / (j *  * µo)				(10)

The terms L and M become complex. The real part must be kept  for the inductance matrix, and the imaginary part for the resistance matrix.

Practically, when the resistance of the earth cable has a value close to the one of the phasor conductors, the influence of its resistance on the reckoning of the inductance may be neglected.

1- 7 - Double circuit three phase line, several wires per phase, resistive soil, two earth cables.

Let us consider the figure 1 of § 11, into which we add the earth cable and its image beyond the mirror.

Vg1 = 0

g1					            g2

ig1

vy1

y1						y2

iy1

vr1

r1						   r2

ir1		dry1	            vb1

b1						   b2

ib1

hr1		 hy1		   hb1

dyb1

- vb1

b'1						b'2

- vr1			        - ib1

r'1						  r'2

- ir1

- vy1

y'1						y'2

- iy1

-vg1 = 0

g'1					            g'2

- ig1

The equation giving the voltage drop on  vr1 is:

dvr1	 µo	  Dr1y'1     diy1	         Dr1b'1     dib1	    Dr1r'1    dir1             Dr1g'1    dig1

= -	   * (Log 	*         +  Log	        * 	      +  Log	  *          + Log	         *

dx         2 *	  Dr1y1       dt	         Dr1b1       dt                  req	       dt               Dr1g1      dt

Dr1y'2     diy2	          Dr1b'2     dib2	      Dr1r'2     dir2   	Dr1g'2    dig2

+ Log 	*          +  Log	         * 	       +   Log	     *          + Log	            * 	)

Dr1y2     dt	           Dr1b2       dt                  req	         dt        	Dr1g2       dt

(1)

in which Dr1y1, Dr1b1... Dr1y2, Dr1b2, ... Dr1g1, Dr2g2 are the distances between the conductor r1 and the conductor y1, ... between the conductor r2 and the conductor y2..., between the conductor r1 and the earth cable g1, ...

The voltage drops on vy1, vb1, vr2, vy2, vb2 are deducted from equation (1) by circular permutation. By putting

µo		  Dr1y'1			        µo		   Dr1r'1

* Log		= r1y1, ...		     * Log		= r1 ...

4 * 		  Dr1y1			      4 * 	      req

We can  write these equations under the following form,

vr1	       r1	    r1y1	   r1b1      r1r2	   r1y2	r1b2	        ir1	      r1g1   r1g2

vy1	       y1r1    y1	   y1b1	   y1r2	   y1y2	y1b2	        iy1	      y1g1    y1g2

d	vb1	       b1r1    b1y1	   b1	   b1r2	   b1y2	b1b2	d       ib1      b1g1	     b1g2           d	    ig1

=					          * 		  +		     *

dx	vr2	       r2r1    r2y1	   r2b1	   r2	   r2y2	r2b2	dt      ir2      r2g1	     r2g2	          dt    ig2

vy2	       y2r1     y2y1	   y2b1	   y2r2	   y2	y2b2	         iy2      y2g1     y2g2

vb2	       b2r1     b2y1	   b2b1	   b2r2	   b2y2	b2	         ib2      b2g1	     b2g2

that we note:

dv			d (i phase)				d(i cdg)

=      A * 			+    	B      *

dx		   	      dt			   	   	  dt

(matrix 6*1)	  (matrix 6*6)	(matrix 6*1)	     (matrix 6*2)		(matrix 2*1)

note: The matrix A is the inductance matrix seen in the formula (1) of § 1-5.

Then we write that the voltage drop on each earth cable is null:

dvg1	   µo	        Dg1r'1     dir1	  Dg1y'1        diy1	 Dg1b'1     dib1	       Dg1g1'      dig1

= -	          * (Log 	       * 	    +  Log	     * 	   +  Log	   	*         + Log	        *

dx	 2 *	        Dg1r1       dt	    Dg1y1         dt             	  Dg1b1      dt		r           dt

Dg1r'2     dir2	      Dg1y'2     diy2	      Dg1b'2    dib2	 Dg1g2'    dig1

+ Log 	          * 	       +  Log	     * 	        +  Log	    *	    + Log	      	*         ) = 0

Dg1r2	 dt	       Dg1y2      dt             	       Dg1b2      dt	               Dg1g2	     dt

Dvg2	   µo	        Dg2r'1     dir1	  Dg2y'1        diy1	 Dg2b'1     dib1	       Dg2g2'      dig2

= -	          * (Log 	       * 	    +  Log	     * 	   +  Log	   	*         + Log	        *

dx	 2 *	        Dg2r1       dt	    Dg2y1         dt             	  Dg2b1      dt		r           dt

Dg2r'2     dir2	      Dg2y'2     diy2	      Dg2b'2    dib2	 Dg2g1'    dig1

+ Log 	          * 	       +  Log	     * 	        +  Log	    *	    + Log	      	*         ) = 0

Dg2r2	 dt	       Dg2y2      dt             	       Dg2b2      dt	               Dg2g1	     dt

(3)

where Dg1g2 is the distance between the earth cable g1 and the earth cable g2, ..., and r the radius of the earth cable.

Iyt i a system of two equations with two unknown  ig1 and ig2. Let us name:

Dg1r'1		        Dg1r'2		        Dg2r'1		        Dg2r'2

Log   	       = r11	Log 	        = r12	Log	        = r21	Log	         = r22

Dg1r1 		         Dg1r2		         Dg2r1		         Dg2r2

Dg1y'1		         Dg1y'2		         Dg2y'1		         Dg2y'2

Log   	        = y11	Log 	         = y12	Log	         = y21	  Log	          = y22

Dg1y1 		         Dg1y2		         Dg2y1		          Dg2y2

Dg1b'1		         Dg1b'2		          Dg2b'1		           Dg2b'2

Log   	       = b11	Log 	          = b12	Log	          = b21	    Log	            = b22

Dg1b1 		         Dg1b2		          Dg2b1		           Dg2b2

Dg1g'1	    	         Dg2g'2		          Dg1g'2	        Dg2g'1

Log	      = g11 	Log                   = g22	  Log	          =  Log	        = g21 = g12

r				r		          Dg1g2	         Dg2g1

the solution is the following one:

ir1

iy1

d    ig1		         1		g22	g11	r11       y11      b11      r21      y21	    b21	   d     	ib1

=  -		         *		         *					            *

dt    ig2	           (g11*g22-g12²)	g12	g11	r12       y12       b12     r22       y22	    b22	   dt        ir2

iy2

ib2

that we note:

d(i cdg)					d(i phase)

-		= 	C     * 	D	*						(4)

dt						     dt

(matrix 2*1)	(matrix 2*2)	(matrix 2*6)	(matrix 6*1)

By reporting equation (4) into the equation (2), we find:

dv									d(i phase)

=      (A  	-   	B     *	C	*	D)	*			(5)

dx		   	    		   	   	  		     dt

matrix 6*1)	  (matrix 6*6)    (matrix 6*2)      (matrix 2*2)	(matrix 2*6)	(matrix 6*1)

The matrix A - B * C * D is the researched inductance matrix.

From figure 1 of this §, we can reckon the different parameters Drr', ..., by formulae similar to (4) of § 16.

Dr1r1' = 2 * (hr1+)		Dr1y'1² = (hr + hy + 2*)² + dry²		Dry² = (hr - hy)² + dry²

Dyy' = 2 * (hy+)			Drb'² = (hr + hb + 2*))² + drb²		Drb² = (hr - hb)² + drb²

Dbb' = 2 * (hb+)		Dyb'² = (hy +hb + 2*)²  + dyb²		Dyb² = (hy - hb)² + dyb²

Dgg' = 2 * (hg+)		Drg'² = (hr + hg + 2*)² + drg²		Drg² = (hr - hg)² + drg²

Dyg'² = (hy + hg + 2*)² + dyg²		Dyg² = (hy - hg)² + dyg²

Dbg'² = (hb + hg + 2*)² + dbg²		Dbg² = (hb - hg)² + dbg²

We can then do the same approximations as at § 15, and check that the factor  seen at § 1-3 and the presence of earth cables have no influence on the positive sequence inductance. On the other hand, the zero sequence inductance increases with the factor d. It is decreased, and so do the mutual zero sequence inductance, by the presence of earth cables.

2 - Capacitance matrix

The capacitance per unit of a double wire line is given by:

1	      1	        	      D		L

=	       	    *  Log	  =

C	2 *  * o    	       r	          o * µo

We can thus admit that the capacitance matrices are deducted from the inductance matrixes by the formula:

 L -1

 C  =

o * µo

3 - Resistance matrix

Through lack of knowledge of the ground resistance, which varies with the nature and the dampness of the soil, and the quality of the earthing sockets of the substations and of the towers, we admit that the resistance matrices are obtained from the inductance matrices by multiplying them by the average ratio between the resistance of  each pair of conductors and the inductance of the loop they form (see figure of § 11).

4 - Matrix of the transverse conductance

This matrix varies strongly with the moisture of the air and of the soil. We choose it so that the Heaviside condition is verified.

(L ( * ( G ( = ( R ( * ( C(

Bibliography [89], [90]