APPENDIX   5

(by clicking above you return to the general summary)

ENCLOSING  OF  A  POWER  TRANSFORMER

By enclosing of an empty transformer, a transient phenomenon  appears. To have a qualitative approach of that, we make the following single phase mock up:

The empty transformer is represented by its magnetising impedance, having a resistance Rµ and an inductance Lµ. The transient functioning of an inductance coil is described at second part, § 131. The instantaneous current value is given by the formula (2) of this §. We study the case where the asymmetry is maximal.

The equation of the voltage on the terminals of the coil, and of the current running inside, is:

Lµ        p

u = U * sin (wt + j)				with j = arctg	       -         0

Rµ        2

-t / t					 	       U		       t

i =  I  *  (e	   - cos w*t)			with I =			*	    0

Rµ² + Lµ²w²	       t

The flux inside the coil, as well as the induction, are proportional to the current i. Now the transformer is reckoned so as in a steady state functioning, when the current has its maximum value I, the induction has a value just beneath its saturation value. By this way, during the transient functioning time lags where i has a value greater than I, the magnetic circuit of the transformer is saturated, and it behaves as a short circuit on the resistance Rµ.

i = u / Rµ

Thus the diagram:

0			10 ms			20 ms			  30 ms

The blue curve represents the voltage on the terminals of the transformer;

The violet curve represents the current in the transformer out of saturation

The yellow curve represents the current in the transformer by taking the saturation into account.

If we transform the current in Fourier series, we find, consequently to the asymmetric peaks, pair rank harmonics.

The alternations in which the peaks are found are seen by the protective relays as representing a fault. On the electromechanical relays as the RXAP, the modules are acted during one alternation, and may release an unwanted tripping after a few periods. On the electronic or digital relays, the measurement is performed at each alternation  and the tripping order is sent only if two consecutive measurements detect a fault. These relays are much less sensitive to this phenomenon.